## Stmap-2
케이블 산출물량
케이블 산출물량
구분
|  |  | #202 |  | 구분 | size(m㎡) | 대상호기 |  |  |  | 총길이(m)
[5 empty] | Stamp-2 | 240 | #201, #204, #205, #207, #209, #210 |  |  |  | 2610
□ 케이블 스케줄표와 실제 케이블 길이와 다를 수 있으므로 현장 실측 후 입찰 요망 ※ 케이블 추가 물량에 대한 추가 정산 없음
ELECTRICAL CABLE SCHEDULE
ROUTE NO. | Serial No. | CABLE NUMBER |  | CABLE SPECIFICATION | [6 empty] | CONDUIT NUMBER | CONDUIT LENGTH [m] | SYSTEM VOLTAGE [kV] | RATING [kW] | LOAD TYPE | FROM |  |  | TO |  |  | ROUTING PATH | ROUTING PATH | [18 empty] | REMARKS
K-TF-112 |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | LENGTH [m] | O.D [mm] | S.A [mm2] | [5 empty] | LOCATION | TAG NUMBER | DESCRIPTION | LOCATION | TAG NUMBER | DESCRIPTION |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  |  | CABLE NO |  |  |  | TO
X | 1 | H-ELTR001-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 25 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-004 | 22.9kV SWGR | 전기실 | EL-TR-001 | 4MVA, 22.9-0.48V STEP-UP TR-1 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109 |  |  | H | ELTR001 | 01 | H-ELTR001-01 | ELTR001 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 2 | H-ELTR001-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 25 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-004 | 22.9kV SWGR | 전기실 | EL-TR-001 | 4MVA, 22.9-0.48V STEP-UP TR-1 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109 |  |  | H | ELTR001 | 02 | H-ELTR001-02 | ELTR001 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 3 | H-ELTR001-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 25 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-004 | 22.9kV SWGR | 전기실 | EL-TR-001 | 4MVA, 22.9-0.48V STEP-UP TR-1 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109 |  |  | H | ELTR001 | 03 | H-ELTR001-03 | ELTR001 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 4 | H-ELTR002-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-005 | 22.9kV SWGR | 전기실 | EL-TR-002 | 4.5MVA, 22.9-0.48V STEP-UP TR-2 | C-TD-106 C-TD-118 C-TD-129 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-129 |  |  | H | ELTR002 | 01 | H-ELTR002-01 | ELTR002 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 5 | H-ELTR002-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-005 | 22.9kV SWGR | 전기실 | EL-TR-002 | 4.5MVA, 22.9-0.48V STEP-UP TR-2 | C-TD-106 C-TD-118 C-TD-129 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-129 |  |  | H | ELTR002 | 02 | H-ELTR002-02 | ELTR002 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 6 | H-ELTR002-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-005 | 22.9kV SWGR | 전기실 | EL-TR-002 | 4.5MVA, 22.9-0.48V STEP-UP TR-2 | C-TD-106 C-TD-118 C-TD-129 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-129 |  |  | H | ELTR002 | 03 | H-ELTR002-03 | ELTR002 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 7 | H-ELTR003-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 20 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-006 | 22.9kV SWGR | 전기실 | EL-TR-003 | 4.5MVA, 22.9-0.48V STEP-UP TR-3 | C-TD-106 C-TD-118 C-TD-128 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-128 |  |  | H | ELTR003 | 01 | H-ELTR003-01 | ELTR003 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 8 | H-ELTR003-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 20 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-006 | 22.9kV SWGR | 전기실 | EL-TR-003 | 4.5MVA, 22.9-0.48V STEP-UP TR-3 | C-TD-106 C-TD-118 C-TD-128 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-128 |  |  | H | ELTR003 | 02 | H-ELTR003-02 | ELTR003 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 9 | H-ELTR003-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 20 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-006 | 22.9kV SWGR | 전기실 | EL-TR-003 | 4.5MVA, 22.9-0.48V STEP-UP TR-3 | C-TD-106 C-TD-118 C-TD-128 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-128 |  |  | H | ELTR003 | 03 | H-ELTR003-03 | ELTR003 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 10 | H-ELTR004-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-007 | 22.9kV SWGR | 전기실 | EL-TR-004 | 4.5MVA, 22.9-0.48V STEP-UP TR-4 | C-TD-106 C-TD-118 C-TD-128 C-TD-138 C-TD-148 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-128; ROUTING PATH 4: C-TD-138; ROUTING PATH 5: C-TD-148 |  |  | H | ELTR004 | 01 | H-ELTR004-01 | ELTR004 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 11 | H-ELTR004-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-007 | 22.9kV SWGR | 전기실 | EL-TR-004 | 4.5MVA, 22.9-0.48V STEP-UP TR-4 | C-TD-106 C-TD-118 C-TD-128 C-TD-138 C-TD-148 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-128; ROUTING PATH 4: C-TD-138; ROUTING PATH 5: C-TD-148 |  |  | H | ELTR004 | 02 | H-ELTR004-02 | ELTR004 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 12 | H-ELTR004-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4500 | F | 전기실 | EL-HV-007 | 22.9kV SWGR | 전기실 | EL-TR-004 | 4.5MVA, 22.9-0.48V STEP-UP TR-4 | C-TD-106 C-TD-118 C-TD-128 C-TD-138 C-TD-148 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TD-118; ROUTING PATH 3: C-TD-128; ROUTING PATH 4: C-TD-138; ROUTING PATH 5: C-TD-148 |  |  | H | ELTR004 | 03 | H-ELTR004-03 | ELTR004 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 13 | H-ELTR005-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 20 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-008 | 22.9kV SWGR | 전기실 | EL-TR-005 | 4MVA, 22.9-0.48V STEP-UP TR-5 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 C-TD-125 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109; ROUTING PATH 5: C-TD-125 |  |  | H | ELTR005 | 01 | H-ELTR005-01 | ELTR005 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 14 | H-ELTR005-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 20 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-008 | 22.9kV SWGR | 전기실 | EL-TR-005 | 4MVA, 22.9-0.48V STEP-UP TR-5 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 C-TD-125 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109; ROUTING PATH 5: C-TD-125 |  |  | H | ELTR005 | 02 | H-ELTR005-02 | ELTR005 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 15 | H-ELTR005-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 20 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-008 | 22.9kV SWGR | 전기실 | EL-TR-005 | 4MVA, 22.9-0.48V STEP-UP TR-5 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 C-TD-125 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109; ROUTING PATH 5: C-TD-125 |  |  | H | ELTR005 | 03 | H-ELTR005-03 | ELTR005 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 16 | H-ELTR006-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 34 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-009 | 22.9kV SWGR | 전기실 | EL-TR-006 | 4MVA, 22.9-0.48V STEP-UP TR-6 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 C-TD-125 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109; ROUTING PATH 5: C-TD-125 |  |  | H | ELTR006 | 01 | H-ELTR006-01 | ELTR006 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 17 | H-ELTR006-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 34 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-009 | 22.9kV SWGR | 전기실 | EL-TR-006 | 4MVA, 22.9-0.48V STEP-UP TR-6 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 C-TD-125 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109; ROUTING PATH 5: C-TD-125 |  |  | H | ELTR006 | 02 | H-ELTR006-02 | ELTR006 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 18 | H-ELTR006-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 34 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-009 | 22.9kV SWGR | 전기실 | EL-TR-006 | 4MVA, 22.9-0.48V STEP-UP TR-6 | C-TD-106 C-TF-105 C-TF-104 C-TD-109 C-TD-125 | ROUTING PATH 1: C-TD-106; ROUTING PATH 2: C-TF-105; ROUTING PATH 3: C-TF-104; ROUTING PATH 4: C-TD-109; ROUTING PATH 5: C-TD-125 |  |  | H | ELTR006 | 03 | H-ELTR006-03 | ELTR006 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 19 | H-ELTR007-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-010 | 22.9kV SWGR | 전기실 | EL-TR-007 | 4MVA, 22.9-0.48V STEP-UP TR-7 | C-TF-105 C-TF-104 C-TD-109 C-TD-125 C-TD-145 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TF-104; ROUTING PATH 3: C-TD-109; ROUTING PATH 4: C-TD-125; ROUTING PATH 5: C-TD-145 |  |  | H | ELTR007 | 01 | H-ELTR007-01 | ELTR007 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 20 | H-ELTR007-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-010 | 22.9kV SWGR | 전기실 | EL-TR-007 | 4MVA, 22.9-0.48V STEP-UP TR-7 | C-TF-105 C-TF-104 C-TD-109 C-TD-125 C-TD-145 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TF-104; ROUTING PATH 3: C-TD-109; ROUTING PATH 4: C-TD-125; ROUTING PATH 5: C-TD-145 |  |  | H | ELTR007 | 02 | H-ELTR007-02 | ELTR007 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 21 | H-ELTR007-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 30 | 39 | 1194.6 | - | - | 22.9 | 4000 | F | 전기실 | EL-HV-010 | 22.9kV SWGR | 전기실 | EL-TR-007 | 4MVA, 22.9-0.48V STEP-UP TR-7 | C-TF-105 C-TF-104 C-TD-109 C-TD-125 C-TD-145 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TF-104; ROUTING PATH 3: C-TD-109; ROUTING PATH 4: C-TD-125; ROUTING PATH 5: C-TD-145 |  |  | H | ELTR007 | 03 | H-ELTR007-03 | ELTR007 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 22 | H-ELTR008-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 26 | 39 | 1194.6 | - | - | 22.9 | 400 | F | 전기실 | EL-HV-011 | 22.9kV SWGR | 전기실 | EL-TR-008 | 400kVA, 22.9-0.38/0.22V AUX TR-1 | C-TF-105 C-TD-111 C-TD-118 C-TD-129 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TD-111; ROUTING PATH 3: C-TD-118; ROUTING PATH 4: C-TD-129 |  |  | H | ELTR008 | 01 | H-ELTR008-01 | ELTR008 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 23 | H-ELTR008-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 26 | 39 | 1194.6 | - | - | 22.9 | 400 | F | 전기실 | EL-HV-011 | 22.9kV SWGR | 전기실 | EL-TR-008 | 400kVA, 22.9-0.38/0.22V AUX TR-1 | C-TF-105 C-TD-111 C-TD-118 C-TD-129 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TD-111; ROUTING PATH 3: C-TD-118; ROUTING PATH 4: C-TD-129 |  |  | H | ELTR008 | 02 | H-ELTR008-02 | ELTR008 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 24 | H-ELTR008-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 26 | 39 | 1194.6 | - | - | 22.9 | 400 | F | 전기실 | EL-HV-011 | 22.9kV SWGR | 전기실 | EL-TR-008 | 400kVA, 22.9-0.38/0.22V AUX TR-1 | C-TF-105 C-TD-111 C-TD-118 C-TD-129 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TD-111; ROUTING PATH 3: C-TD-118; ROUTING PATH 4: C-TD-129 |  |  | H | ELTR008 | 03 | H-ELTR008-03 | ELTR008 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 25 | H-ELTR009-01 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 26 | 39 | 1194.6 | - | - | 22.9 | 400 | F | 전기실 | EL-HV-012 | 22.9kV SWGR | 전기실 | EL-TR-009 | 400kVA, 22.9-0.38/0.22V AUX TR-2 | C-TF-105 C-TD-111 C-TD-118 C-TD-128 C-TD-130 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TD-111; ROUTING PATH 3: C-TD-118; ROUTING PATH 4: C-TD-128; ROUTING PATH 5: C-TD-130 |  |  | H | ELTR009 | 01 | H-ELTR009-01 | ELTR008 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 26 | H-ELTR009-02 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 26 | 39 | 1194.6 | - | - | 22.9 | 400 | F | 전기실 | EL-HV-012 | 22.9kV SWGR | 전기실 | EL-TR-009 | 400kVA, 22.9-0.38/0.22V AUX TR-2 | C-TF-105 C-TD-111 C-TD-118 C-TD-128 C-TD-130 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TD-111; ROUTING PATH 3: C-TD-118; ROUTING PATH 4: C-TD-128; ROUTING PATH 5: C-TD-130 |  |  | H | ELTR009 | 02 | H-ELTR009-02 | ELTR008 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | 27 | H-ELTR009-03 | P | 22.9kV | FR-CN/CO-W | 1C | 100 | 26 | 39 | 1194.6 | - | - | 22.9 | 400 | F | 전기실 | EL-HV-012 | 22.9kV SWGR | 전기실 | EL-TR-009 | 400kVA, 22.9-0.38/0.22V AUX TR-2 | C-TF-105 C-TD-111 C-TD-118 C-TD-128 C-TD-130 | ROUTING PATH 1: C-TF-105; ROUTING PATH 2: C-TD-111; ROUTING PATH 3: C-TD-118; ROUTING PATH 4: C-TD-128; ROUTING PATH 5: C-TD-130 |  |  | H | ELTR009 | 03 | H-ELTR009-03 | ELTR008 | 22.9kV FR-CN/CO-W 1C-100㎟-P
X | [9 empty] | #VALUE!
X | 28 | L-SOFC101-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 38 | 24 | 452.39 | K-PC-002 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC101 | 01 | L-SOFC101-01 | SOFC101 | 0.6/1kV FR-CV 1C-185㎟-P
X | 29 | L-SOFC101-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 38 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC101 | 02 | L-SOFC101-02 | SOFC101 | 0.6/1kV FR-CV 1C-185㎟-P
X | 30 | L-SOFC101-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 38 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC101 | 03 | L-SOFC101-03 | SOFC101 | 0.6/1kV FR-CV 1C-185㎟-P
X | 31 | L-SOFC101-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 38 | 24 | 452.39 | K-PC-003 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC101 | 04 | L-SOFC101-04 | SOFC101 | 0.6/1kV FR-CV 1C-185㎟-P
X | 32 | L-SOFC101-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 38 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC101 | 05 | L-SOFC101-05 | SOFC101 | 0.6/1kV FR-CV 1C-185㎟-P
X | 33 | L-SOFC101-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 38 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC101 | 06 | L-SOFC101-06 | SOFC101 | 0.6/1kV FR-CV 1C-185㎟-P
X | 34 | L-SOFC102-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 35 | 24 | 452.39 | K-PC-051 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC102 | 01 | L-SOFC102-01 | SOFC102 | 0.6/1kV FR-CV 1C-185㎟-P
X | 35 | L-SOFC102-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 35 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC102 | 02 | L-SOFC102-02 | SOFC102 | 0.6/1kV FR-CV 1C-185㎟-P
X | 36 | L-SOFC102-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 35 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC102 | 03 | L-SOFC102-03 | SOFC102 | 0.6/1kV FR-CV 1C-185㎟-P
X | 37 | L-SOFC102-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 35 | 24 | 452.39 | K-PC-052 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC102 | 04 | L-SOFC102-04 | SOFC102 | 0.6/1kV FR-CV 1C-185㎟-P
X | 38 | L-SOFC102-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 35 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC102 | 05 | L-SOFC102-05 | SOFC102 | 0.6/1kV FR-CV 1C-185㎟-P
X | 39 | L-SOFC102-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 35 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | K-TF-455 K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-207; ROUTING PATH 3: K-TF-212 |  |  | L | SOFC102 | 06 | L-SOFC102-06 | SOFC102 | 0.6/1kV FR-CV 1C-185㎟-P
O | 40 | L-SOFC103-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 36 | 24 | 452.39 | K-PC-093 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC103 | 01 | L-SOFC103-01 | SOFC103 | 0.6/1kV FR-CV 1C-185㎟-P
O | 41 | L-SOFC103-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 36 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC103 | 02 | L-SOFC103-02 | SOFC103 | 0.6/1kV FR-CV 1C-185㎟-P
O | 42 | L-SOFC103-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 36 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC103 | 03 | L-SOFC103-03 | SOFC103 | 0.6/1kV FR-CV 1C-185㎟-P
O | 43 | L-SOFC103-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 36 | 24 | 452.39 | K-PC-094 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC103 | 04 | L-SOFC103-04 | SOFC103 | 0.6/1kV FR-CV 1C-185㎟-P
O | 44 | L-SOFC103-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 36 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC103 | 05 | L-SOFC103-05 | SOFC103 | 0.6/1kV FR-CV 1C-185㎟-P
O | 45 | L-SOFC103-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 36 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC103 | 06 | L-SOFC103-06 | SOFC103 | 0.6/1kV FR-CV 1C-185㎟-P
O | 46 | L-SOFC104-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 37 | 24 | 452.39 | K-PC-131 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC104 | 01 | L-SOFC104-01 | SOFC104 | 0.6/1kV FR-CV 1C-185㎟-P
O | 47 | L-SOFC104-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 37 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC104 | 02 | L-SOFC104-02 | SOFC104 | 0.6/1kV FR-CV 1C-185㎟-P
O | 48 | L-SOFC104-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 37 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC104 | 03 | L-SOFC104-03 | SOFC104 | 0.6/1kV FR-CV 1C-185㎟-P
O | 49 | L-SOFC104-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 37 | 24 | 452.39 | K-PC-132 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC104 | 04 | L-SOFC104-04 | SOFC104 | 0.6/1kV FR-CV 1C-185㎟-P
O | 50 | L-SOFC104-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 37 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC104 | 05 | L-SOFC104-05 | SOFC104 | 0.6/1kV FR-CV 1C-185㎟-P
O | 51 | L-SOFC104-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 37 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | K-TF-455 K-TF-107 K-TF-112 | ROUTING PATH 1: K-TF-455; ROUTING PATH 2: K-TF-107; ROUTING PATH 3: K-TF-112 |  |  | L | SOFC104 | 06 | L-SOFC104-06 | SOFC104 | 0.6/1kV FR-CV 1C-185㎟-P
X | 52 | L-SOFC105-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 40 | 24 | 452.39 | K-PC-201 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | K-TF-456 K-TF-208 K-TF-212 K-PC-555 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-555 |  |  | L | SOFC105 | 01 | L-SOFC105-01 | SOFC105 | 0.6/1kV FR-CV 1C-185㎟-P
X | 53 | L-SOFC105-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 40 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | K-TF-456 K-TF-208 K-TF-212 K-PC-555 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-555 |  |  | L | SOFC105 | 02 | L-SOFC105-02 | SOFC105 | 0.6/1kV FR-CV 1C-185㎟-P
X | 54 | L-SOFC105-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 40 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | K-TF-456 K-TF-208 K-TF-212 K-PC-555 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-555 |  |  | L | SOFC105 | 03 | L-SOFC105-03 | SOFC105 | 0.6/1kV FR-CV 1C-185㎟-P
X | 55 | L-SOFC105-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 40 | 24 | 452.39 | K-PC-202 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | K-TF-456 K-TF-208 K-TF-212 K-PC-554 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-554 |  |  | L | SOFC105 | 04 | L-SOFC105-04 | SOFC105 | 0.6/1kV FR-CV 1C-185㎟-P
X | 56 | L-SOFC105-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 40 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | K-TF-456 K-TF-208 K-TF-212 K-PC-554 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-554 |  |  | L | SOFC105 | 05 | L-SOFC105-05 | SOFC105 | 0.6/1kV FR-CV 1C-185㎟-P
X | 57 | L-SOFC105-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 40 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | K-TF-456 K-TF-208 K-TF-212 K-PC-554 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-554 |  |  | L | SOFC105 | 06 | L-SOFC105-06 | SOFC105 | 0.6/1kV FR-CV 1C-185㎟-P
X | 58 | L-SOFC106-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 43 | 24 | 452.39 | K-PC-241 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | K-TF-456 K-TF-208 K-TF-212 K-PC-553 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-553 |  |  | L | SOFC106 | 01 | L-SOFC106-01 | SOFC106 | 0.6/1kV FR-CV 1C-185㎟-P
X | 59 | L-SOFC106-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 43 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | K-TF-456 K-TF-208 K-TF-212 K-PC-553 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-553 |  |  | L | SOFC106 | 02 | L-SOFC106-02 | SOFC106 | 0.6/1kV FR-CV 1C-185㎟-P
X | 60 | L-SOFC106-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 43 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | K-TF-456 K-TF-208 K-TF-212 K-PC-553 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-553 |  |  | L | SOFC106 | 03 | L-SOFC106-03 | SOFC106 | 0.6/1kV FR-CV 1C-185㎟-P
X | 61 | L-SOFC106-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 43 | 24 | 452.39 | K-PC-242 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | K-TF-456 K-TF-208 K-TF-212 K-PC-552 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-552 |  |  | L | SOFC106 | 04 | L-SOFC106-04 | SOFC106 | 0.6/1kV FR-CV 1C-185㎟-P
X | 62 | L-SOFC106-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 43 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | K-TF-456 K-TF-208 K-TF-212 K-PC-552 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-552 |  |  | L | SOFC106 | 05 | L-SOFC106-05 | SOFC106 | 0.6/1kV FR-CV 1C-185㎟-P
X | 63 | L-SOFC106-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 43 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | K-TF-456 K-TF-208 K-TF-212 K-PC-552 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-208; ROUTING PATH 3: K-TF-212; ROUTING PATH 4: K-PC-552 |  |  | L | SOFC106 | 06 | L-SOFC106-06 | SOFC106 | 0.6/1kV FR-CV 1C-185㎟-P
O | 64 | L-SOFC107-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 | K-PC-282 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | K-TF-456 K-TF-108 K-TF-112 K-PC-562 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-562 |  |  | L | SOFC107 | 01 | L-SOFC107-01 | SOFC107 | 0.6/1kV FR-CV 1C-185㎟-P
O | 65 | L-SOFC107-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | K-TF-456 K-TF-108 K-TF-112 K-PC-562 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-562 |  |  | L | SOFC107 | 02 | L-SOFC107-02 | SOFC107 | 0.6/1kV FR-CV 1C-185㎟-P
O | 66 | L-SOFC107-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | K-TF-456 K-TF-108 K-TF-112 K-PC-562 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-562 |  |  | L | SOFC107 | 03 | L-SOFC107-03 | SOFC107 | 0.6/1kV FR-CV 1C-185㎟-P
O | 67 | L-SOFC107-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 | K-PC-283 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | K-TF-456 K-TF-108 K-TF-112 K-PC-563 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-563 |  |  | L | SOFC107 | 04 | L-SOFC107-04 | SOFC107 | 0.6/1kV FR-CV 1C-185㎟-P
O | 68 | L-SOFC107-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | K-TF-456 K-TF-108 K-TF-112 K-PC-563 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-563 |  |  | L | SOFC107 | 05 | L-SOFC107-05 | SOFC107 | 0.6/1kV FR-CV 1C-185㎟-P
O | 69 | L-SOFC107-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | K-TF-456 K-TF-108 K-TF-112 K-PC-563 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-563 |  |  | L | SOFC107 | 06 | L-SOFC107-06 | SOFC107 | 0.6/1kV FR-CV 1C-185㎟-P
O | 70 | L-SOFC108-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 | K-PC-331 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | K-TF-456 K-TF-108 K-TF-112 K-PC-565 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-565 |  |  | L | SOFC108 | 01 | L-SOFC108-01 | SOFC108 | 0.6/1kV FR-CV 1C-185㎟-P
O | 71 | L-SOFC108-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | K-TF-456 K-TF-108 K-TF-112 K-PC-565 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-565 |  |  | L | SOFC108 | 02 | L-SOFC108-02 | SOFC108 | 0.6/1kV FR-CV 1C-185㎟-P
O | 72 | L-SOFC108-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | K-TF-456 K-TF-108 K-TF-112 K-PC-565 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-565 |  |  | L | SOFC108 | 03 | L-SOFC108-03 | SOFC108 | 0.6/1kV FR-CV 1C-185㎟-P
O | 73 | L-SOFC108-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 | K-PC-332 | 13 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | K-TF-456 K-TF-108 K-TF-112 K-PC-564 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-564 |  |  | L | SOFC108 | 04 | L-SOFC108-04 | SOFC108 | 0.6/1kV FR-CV 1C-185㎟-P
O | 74 | L-SOFC108-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | K-TF-456 K-TF-108 K-TF-112 K-PC-564 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-564 |  |  | L | SOFC108 | 05 | L-SOFC108-05 | SOFC108 | 0.6/1kV FR-CV 1C-185㎟-P
O | 75 | L-SOFC108-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | K-TF-456 K-TF-108 K-TF-112 K-PC-564 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-564 |  |  | L | SOFC108 | 06 | L-SOFC108-06 | SOFC108 | 0.6/1kV FR-CV 1C-185㎟-P
O | 76 | L-SOFC109-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 | K-PC-501 | 16 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | K-TF-456 K-TF-108 K-TF-112 K-PC-551 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-551 |  |  | L | SOFC109 | 01 | L-SOFC109-01 | SOFC109 | 0.6/1kV FR-CV 1C-185㎟-P
O | 77 | L-SOFC109-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | K-TF-456 K-TF-108 K-TF-112 K-PC-551 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-551 |  |  | L | SOFC109 | 02 | L-SOFC109-02 | SOFC109 | 0.6/1kV FR-CV 1C-185㎟-P
O | 78 | L-SOFC109-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | K-TF-456 K-TF-108 K-TF-112 K-PC-551 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-551 |  |  | L | SOFC109 | 03 | L-SOFC109-03 | SOFC109 | 0.6/1kV FR-CV 1C-185㎟-P
O | 79 | L-SOFC109-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 | K-PC-502 | 16 | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | K-TF-456 K-TF-108 K-TF-112 K-PC-561 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-561 |  |  | L | SOFC109 | 04 | L-SOFC109-04 | SOFC109 | 0.6/1kV FR-CV 1C-185㎟-P
O | 80 | L-SOFC109-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | K-TF-456 K-TF-108 K-TF-112 K-PC-561 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-561 |  |  | L | SOFC109 | 05 | L-SOFC109-05 | SOFC109 | 0.6/1kV FR-CV 1C-185㎟-P
O | 81 | L-SOFC109-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-102 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | K-TF-456 K-TF-108 K-TF-112 K-PC-561 | ROUTING PATH 1: K-TF-456; ROUTING PATH 2: K-TF-108; ROUTING PATH 3: K-TF-112; ROUTING PATH 4: K-PC-561 |  |  | L | SOFC109 | 06 | L-SOFC109-06 | SOFC109 | 0.6/1kV FR-CV 1C-185㎟-P
X | 82 | L-WDM101-01 | P | 0.6/1kV | FR-CV | 2C | 10 | 40 | 17 | 226.99 | K-PB-402 | 19 | 0.12 | 1.2 | F | 전기실 | EL-LV-103 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #101 | WATER DISTRIBUTION MODULE #101 | K-TF-107 K-TF-102 | ROUTING PATH 1: K-TF-107; ROUTING PATH 2: K-TF-102 |  |  | L | WDM101 | 01 | L-WDM101-01 | WDM101 | 0.6/1kV FR-CV 2C-10㎟-P
X | 83 | L-WDM102-02 | P | 0.6/1kV | FR-CV | 2C | 10 | 42 | 17 | 226.99 | K-PB-403 | 17 | 0.12 | 1.2 | F | 전기실 | EL-LV-103 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #102 | WATER DISTRIBUTION MODULE #102 | K-TF-107 K-TF-102 | ROUTING PATH 1: K-TF-107; ROUTING PATH 2: K-TF-102 |  |  | L | WDM102 | 02 | L-WDM102-02 | WDM102 | 0.6/1kV FR-CV 2C-10㎟-P
X | 84 | L-TC101-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 38 | 22 | 380.14 | K-PB-404 | 15 | 0.12 | 2.04 | F | 전기실 | EL-LV-103 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | TC #101 | TELE CABINET #101 | K-TF-107 K-TF-102 | ROUTING PATH 1: K-TF-107; ROUTING PATH 2: K-TF-102 |  |  | L | TC101 | 01 | L-TC101-01 | TC101 | 0.6/1kV FR-CV 2C-25㎟-P
X | 85 | L-EHT101-01 | P | 0.6/1kV | FR-CV | 2C | 6 | 39 | 14 | 153.94 | K-PB-001 | 13 | 0.12 | 0.375 | F | 전기실 | EL-LV-103 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #101 | FUEL CELL EHT #101 | K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-207; ROUTING PATH 2: K-TF-212 |  |  | L | EHT101 | 01 | L-EHT101-01 | EHT101 | 0.6/1kV FR-CV 2C-6㎟-P
X | 86 | L-EHT102-02 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-004 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #101 | FUEL CELL EHT #101 | FUEL CELL AREA | EHT #102 | FUEL CELL EHT #102 | - | [21 empty] | L | EHT102 | 02 | L-EHT102-02 | EHT102 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 87 | L-EHT103-03 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-005 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #102 | FUEL CELL EHT #102 | FUEL CELL AREA | EHT #103 | FUEL CELL EHT #103 | - | [21 empty] | L | EHT103 | 03 | L-EHT103-03 | EHT103 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 88 | L-EHT104-04 | P | 0.6/1kV | FR-CV | 2C | 6 | 35 | 14 | 153.94 | K-PB-133 | 13 | 0.12 | 0.375 | F | 전기실 | EL-LV-103 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #104 | FUEL CELL EHT #104 | K-TF-107 K-TF-102 | ROUTING PATH 1: K-TF-107; ROUTING PATH 2: K-TF-102 |  |  | L | EHT104 | 04 | L-EHT104-04 | EHT104 | 0.6/1kV FR-CV 2C-6㎟-P
X | 89 | L-EHT105-05 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-134 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #104 | FUEL CELL EHT #104 | FUEL CELL AREA | EHT #105 | FUEL CELL EHT #105 | - | [21 empty] | L | EHT105 | 05 | L-EHT105-05 | EHT105 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 90 | L-EHT106-06 | P | 0.6/1kV | FR-CV | 2C | 6 | 11 | 14 | 153.94 | K-PA-135 | 11 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #105 | FUEL CELL EHT #105 | FUEL CELL AREA | EHT #106 | FUEL CELL EHT #106 | - | [21 empty] | L | EHT106 | 06 | L-EHT106-06 | EHT106 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 91 | L-EHT107-07 | P | 0.6/1kV | FR-CV | 2C | 6 | 45 | 14 | 153.94 | K-PB-281 | 13 | 0.12 | 0.375 | F | 전기실 | EL-LV-103 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #107 | FUEL CELL EHT #107 | K-TF-207 K-TF-212 | ROUTING PATH 1: K-TF-207; ROUTING PATH 2: K-TF-212 |  |  | L | EHT107 | 07 | L-EHT107-07 | EHT107 | 0.6/1kV FR-CV 2C-6㎟-P
X | 92 | L-EHT108-08 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-284 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #107 | FUEL CELL EHT #107 | FUEL CELL AREA | EHT #108 | FUEL CELL EHT #108 | - | [21 empty] | L | EHT108 | 08 | L-EHT108-08 | EHT108 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 93 | L-EHT109-09 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-285 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #108 | FUEL CELL EHT #108 | FUEL CELL AREA | EHT #109 | FUEL CELL EHT #109 | - | [21 empty] | L | EHT109 | 09 | L-EHT109-09 | EHT109 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X
X | 94 | L-SOFC201-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 55 | 24 | 452.39 | K-PC-411 | 24 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC201 | 01 | L-SOFC201-01 | SOFC201 | 0.6/1kV FR-CV 1C-185㎟-P
X | 95 | L-SOFC201-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 55 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC201 | 02 | L-SOFC201-02 | SOFC201 | 0.6/1kV FR-CV 1C-185㎟-P
X | 96 | L-SOFC201-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 55 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC201 | 03 | L-SOFC201-03 | SOFC201 | 0.6/1kV FR-CV 1C-185㎟-P
X | 97 | L-SOFC201-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 55 | 24 | 452.39 | K-PC-412 | 24 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC201 | 04 | L-SOFC201-04 | SOFC201 | 0.6/1kV FR-CV 1C-185㎟-P
X | 98 | L-SOFC201-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 55 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC201 | 05 | L-SOFC201-05 | SOFC201 | 0.6/1kV FR-CV 1C-185㎟-P
X | 99 | L-SOFC201-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 55 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC201 | 06 | L-SOFC201-06 | SOFC201 | 0.6/1kV FR-CV 1C-185㎟-P
X | 100 | L-SOFC202-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 52 | 24 | 452.39 | K-PC-013 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC202 | 01 | L-SOFC202-01 | SOFC202 | 0.6/1kV FR-CV 1C-185㎟-P
X | 101 | L-SOFC202-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 52 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC202 | 02 | L-SOFC202-02 | SOFC202 | 0.6/1kV FR-CV 1C-185㎟-P
X | 102 | L-SOFC202-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 52 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC202 | 03 | L-SOFC202-03 | SOFC202 | 0.6/1kV FR-CV 1C-185㎟-P
X | 103 | L-SOFC202-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 52 | 24 | 452.39 | K-PC-014 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC202 | 04 | L-SOFC202-04 | SOFC202 | 0.6/1kV FR-CV 1C-185㎟-P
X | 104 | L-SOFC202-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 52 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC202 | 05 | L-SOFC202-05 | SOFC202 | 0.6/1kV FR-CV 1C-185㎟-P
X | 105 | L-SOFC202-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 52 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC202 | 06 | L-SOFC202-06 | SOFC202 | 0.6/1kV FR-CV 1C-185㎟-P
X | 106 | L-SOFC203-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 49 | 24 | 452.39 | K-PC-061 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC203 | 01 | L-SOFC203-01 | SOFC203 | 0.6/1kV FR-CV 1C-185㎟-P
X | 107 | L-SOFC203-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 49 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC203 | 02 | L-SOFC203-02 | SOFC203 | 0.6/1kV FR-CV 1C-185㎟-P
X | 108 | L-SOFC203-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 49 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC203 | 03 | L-SOFC203-03 | SOFC203 | 0.6/1kV FR-CV 1C-185㎟-P
X | 109 | L-SOFC203-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 49 | 24 | 452.39 | K-PC-062 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC203 | 04 | L-SOFC203-04 | SOFC203 | 0.6/1kV FR-CV 1C-185㎟-P
X | 110 | L-SOFC203-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 49 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC203 | 05 | L-SOFC203-05 | SOFC203 | 0.6/1kV FR-CV 1C-185㎟-P
X | 111 | L-SOFC203-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 49 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | K-TF-459 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | SOFC203 | 06 | L-SOFC203-06 | SOFC203 | 0.6/1kV FR-CV 1C-185㎟-P
X | 112 | L-SOFC204-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 46 | 24 | 452.39 | K-PC-091 | 22 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC204 | 01 | L-SOFC204-01 | SOFC204 | 0.6/1kV FR-CV 1C-185㎟-P
X | 113 | L-SOFC204-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 46 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC204 | 02 | L-SOFC204-02 | SOFC204 | 0.6/1kV FR-CV 1C-185㎟-P
X | 114 | L-SOFC204-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 46 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC204 | 03 | L-SOFC204-03 | SOFC204 | 0.6/1kV FR-CV 1C-185㎟-P
X | 115 | L-SOFC204-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 46 | 24 | 452.39 | K-PC-092 | 22 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC204 | 04 | L-SOFC204-04 | SOFC204 | 0.6/1kV FR-CV 1C-185㎟-P
X | 116 | L-SOFC204-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 46 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC204 | 05 | L-SOFC204-05 | SOFC204 | 0.6/1kV FR-CV 1C-185㎟-P
X | 117 | L-SOFC204-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 46 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC204 | 06 | L-SOFC204-06 | SOFC204 | 0.6/1kV FR-CV 1C-185㎟-P
X | 118 | L-SOFC205-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 | K-PC-141 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC205 | 01 | L-SOFC205-01 | SOFC205 | 0.6/1kV FR-CV 1C-185㎟-P
X | 119 | L-SOFC205-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC205 | 02 | L-SOFC205-02 | SOFC205 | 0.6/1kV FR-CV 1C-185㎟-P
X | 120 | L-SOFC205-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC205 | 03 | L-SOFC205-03 | SOFC205 | 0.6/1kV FR-CV 1C-185㎟-P
X | 121 | L-SOFC205-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 | K-PC-142 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC205 | 04 | L-SOFC205-04 | SOFC205 | 0.6/1kV FR-CV 1C-185㎟-P
X | 122 | L-SOFC205-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC205 | 05 | L-SOFC205-05 | SOFC205 | 0.6/1kV FR-CV 1C-185㎟-P
X | 123 | L-SOFC205-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | K-TF-459 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-459; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC205 | 06 | L-SOFC205-06 | SOFC205 | 0.6/1kV FR-CV 1C-185㎟-P
X | 124 | L-SOFC206-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 | K-PC-213 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | K-TF-460 K-TF-227 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC206 | 01 | L-SOFC206-01 | SOFC206 | 0.6/1kV FR-CV 1C-185㎟-P
X | 125 | L-SOFC206-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | K-TF-460 K-TF-227 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC206 | 02 | L-SOFC206-02 | SOFC206 | 0.6/1kV FR-CV 1C-185㎟-P
X | 126 | L-SOFC206-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | K-TF-460 K-TF-227 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC206 | 03 | L-SOFC206-03 | SOFC206 | 0.6/1kV FR-CV 1C-185㎟-P
X | 127 | L-SOFC206-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 | K-PC-214 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | K-TF-460 K-TF-227 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC206 | 04 | L-SOFC206-04 | SOFC206 | 0.6/1kV FR-CV 1C-185㎟-P
X | 128 | L-SOFC206-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | K-TF-460 K-TF-227 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC206 | 05 | L-SOFC206-05 | SOFC206 | 0.6/1kV FR-CV 1C-185㎟-P
X | 129 | L-SOFC206-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 42 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | K-TF-460 K-TF-227 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC206 | 06 | L-SOFC206-06 | SOFC206 | 0.6/1kV FR-CV 1C-185㎟-P
X | 130 | L-SOFC207-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 | K-PC-251 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC207 | 01 | L-SOFC207-01 | SOFC207 | 0.6/1kV FR-CV 1C-185㎟-P
X | 131 | L-SOFC207-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC207 | 02 | L-SOFC207-02 | SOFC207 | 0.6/1kV FR-CV 1C-185㎟-P
X | 132 | L-SOFC207-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC207 | 03 | L-SOFC207-03 | SOFC207 | 0.6/1kV FR-CV 1C-185㎟-P
X | 133 | L-SOFC207-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 | K-PC-252 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC207 | 04 | L-SOFC207-04 | SOFC207 | 0.6/1kV FR-CV 1C-185㎟-P
X | 134 | L-SOFC207-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC207 | 05 | L-SOFC207-05 | SOFC207 | 0.6/1kV FR-CV 1C-185㎟-P
X | 135 | L-SOFC207-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 45 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC207 | 06 | L-SOFC207-06 | SOFC207 | 0.6/1kV FR-CV 1C-185㎟-P
X | 136 | L-SOFC208-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 | K-PC-294 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC208 | 01 | L-SOFC208-01 | SOFC208 | 0.6/1kV FR-CV 1C-185㎟-P
X | 137 | L-SOFC208-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC208 | 02 | L-SOFC208-02 | SOFC208 | 0.6/1kV FR-CV 1C-185㎟-P
X | 138 | L-SOFC208-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC208 | 03 | L-SOFC208-03 | SOFC208 | 0.6/1kV FR-CV 1C-185㎟-P
X | 139 | L-SOFC208-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 | K-PC-295 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC208 | 04 | L-SOFC208-04 | SOFC208 | 0.6/1kV FR-CV 1C-185㎟-P
X | 140 | L-SOFC208-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC208 | 05 | L-SOFC208-05 | SOFC208 | 0.6/1kV FR-CV 1C-185㎟-P
X | 141 | L-SOFC208-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 48 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | K-TF-460 K-TF-127 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC208 | 06 | L-SOFC208-06 | SOFC208 | 0.6/1kV FR-CV 1C-185㎟-P
X | 142 | L-SOFC209-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 | K-PC-341 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC209 | 01 | L-SOFC209-01 | SOFC209 | 0.6/1kV FR-CV 1C-185㎟-P
X | 143 | L-SOFC209-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC209 | 02 | L-SOFC209-02 | SOFC209 | 0.6/1kV FR-CV 1C-185㎟-P
X | 144 | L-SOFC209-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC209 | 03 | L-SOFC209-03 | SOFC209 | 0.6/1kV FR-CV 1C-185㎟-P
X | 145 | L-SOFC209-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 | K-PC-342 | 21 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC209 | 04 | L-SOFC209-04 | SOFC209 | 0.6/1kV FR-CV 1C-185㎟-P
X | 146 | L-SOFC209-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC209 | 05 | L-SOFC209-05 | SOFC209 | 0.6/1kV FR-CV 1C-185㎟-P
X | 147 | L-SOFC209-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 51 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC209 | 06 | L-SOFC209-06 | SOFC209 | 0.6/1kV FR-CV 1C-185㎟-P
X | 148 | L-SOFC210-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 57 | 24 | 452.39 | K-PC-503 | 26 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC210 | 01 | L-SOFC210-01 | SOFC210 | 0.6/1kV FR-CV 1C-185㎟-P
X | 149 | L-SOFC210-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 57 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC210 | 02 | L-SOFC210-02 | SOFC210 | 0.6/1kV FR-CV 1C-185㎟-P
X | 150 | L-SOFC210-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 57 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC210 | 03 | L-SOFC210-03 | SOFC210 | 0.6/1kV FR-CV 1C-185㎟-P
X | 151 | L-SOFC210-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 57 | 24 | 452.39 | K-PC-504 | 26 | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC210 | 04 | L-SOFC210-04 | SOFC210 | 0.6/1kV FR-CV 1C-185㎟-P
X | 152 | L-SOFC210-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 57 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC210 | 05 | L-SOFC210-05 | SOFC210 | 0.6/1kV FR-CV 1C-185㎟-P
X | 153 | L-SOFC210-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 57 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-202 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | K-TF-460 K-TF-127 K-TF-147 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-460; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-147; ROUTING PATH 4: K-TF-150; ROUTING PATH 5: K-TF-149 |  |  | L | SOFC210 | 06 | L-SOFC210-06 | SOFC210 | 0.6/1kV FR-CV 1C-185㎟-P
X | 154 | L-WDM201-01 | P | 0.6/1kV | FR-CV | 2C | 10 | 51 | 17 | 226.99 | K-PB-413 | 28 | 0.12 | 1.2 | F | 전기실 | EL-LV-203 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #201 | WATER DISTRIBUTION MODULE #201 | K-TF-226 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-226; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | WDM201 | 01 | L-WDM201-01 | WDM201 | 0.6/1kV FR-CV 2C-10㎟-P
X | 155 | L-WDM202-02 | P | 0.6/1kV | FR-CV | 2C | 10 | 53 | 17 | 226.99 | K-PB-414 | 27 | 0.12 | 1.2 | F | 전기실 | EL-LV-203 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #202 | WATER DISTRIBUTION MODULE #202 | K-TF-226 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-226; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | WDM202 | 02 | L-WDM202-02 | WDM202 | 0.6/1kV FR-CV 2C-10㎟-P
X | 156 | L-TC201-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 49 | 22 | 380.14 | K-PB-401 | 25 | 0.12 | 2.04 | F | 전기실 | EL-LV-203 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | TC #201 | TELE CABINET #201 | K-TF-226 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-226; ROUTING PATH 2: K-TF-220; ROUTING PATH 3: K-TF-219 |  |  | L | TC201 | 01 | L-TC201-01 | TC201 | 0.6/1kV FR-CV 2C-25㎟-P
O | 157 | L-EHT204-04 | P | 0.6/1kV | FR-CV | 2C | 6 | 41 | 14 | 153.94 | K-PB-104 | 22 | 0.12 | 0.5 | F | 전기실 | EL-LV-203 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #204 | FUEL CELL EHT #204 | K-TF-126 K-TF-120 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-126; ROUTING PATH 2: K-TF-120; ROUTING PATH 3: K-TF-116; ROUTING PATH 4: K-TF-112 |  |  | L | EHT204 | 04 | L-EHT204-04 | EHT204 | 0.6/1kV FR-CV 2C-6㎟-P
X | 158 | L-EHT203-03 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-105 | 8 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #204 | FUEL CELL EHT #204 | FUEL CELL AREA | EHT #203 | FUEL CELL EHT #203 | - | [21 empty] | L | EHT203 | 03 | L-EHT203-03 | EHT203 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 159 | L-EHT202-02 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-106 | 10 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #203 | FUEL CELL EHT #203 | FUEL CELL AREA | EHT #202 | FUEL CELL EHT #202 | - | [21 empty] | L | EHT202 | 02 | L-EHT202-02 | EHT202 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 160 | L-EHT201-01 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-107 | 8 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #202 | FUEL CELL EHT #202 | FUEL CELL AREA | EHT #201 | FUEL CELL EHT #201 | - | [21 empty] | L | EHT201 | 01 | L-EHT201-01 | EHT201 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
O | 161 | L-EHT205-05 | P | 0.6/1kV | FR-CV | 2C | 6 | 40 | 14 | 153.94 | K-PB-143 | 21 | 0.12 | 0.375 | F | 전기실 | EL-LV-203 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #205 | FUEL CELL EHT #205 | K-TF-126 K-TF-120 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-126; ROUTING PATH 2: K-TF-120; ROUTING PATH 3: K-TF-116; ROUTING PATH 4: K-TF-112 |  |  | L | EHT205 | 05 | L-EHT205-05 | EHT205 | 0.6/1kV FR-CV 2C-6㎟-P
X | 162 | L-EHT206-06 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-146 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #205 | FUEL CELL EHT #205 | FUEL CELL AREA | EHT #206 | FUEL CELL EHT #206 | - | [21 empty] | L | EHT206 | 06 | L-EHT206-06 | EHT206 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 163 | L-EHT207-07 | P | 0.6/1kV | FR-CV | 2C | 6 | 11 | 14 | 153.94 | K-PA-147 | 11 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #206 | FUEL CELL EHT #206 | FUEL CELL AREA | EHT #207 | FUEL CELL EHT #207 | - | [21 empty] | L | EHT207 | 07 | L-EHT207-07 | EHT207 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 164 | L-EHT208-08 | P | 0.6/1kV | FR-CV | 2C | 6 | 50 | 14 | 153.94 | K-PB-293 | 21 | 0.12 | 0.375 | F | 전기실 | EL-LV-203 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #208 | FUEL CELL EHT #208 | K-TF-126 K-TF-120 K-TF-123 K-TF-122 | ROUTING PATH 1: K-TF-126; ROUTING PATH 2: K-TF-120; ROUTING PATH 3: K-TF-123; ROUTING PATH 4: K-TF-122 |  |  | L | EHT208 | 08 | L-EHT208-08 | EHT208 | 0.6/1kV FR-CV 2C-6㎟-P
X | 165 | L-EHT209-09 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-296 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #208 | FUEL CELL EHT #208 | FUEL CELL AREA | EHT #209 | FUEL CELL EHT #209 | - | [21 empty] | L | EHT209 | 09 | L-EHT209-09 | EHT209 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 166 | L-EHT210-10 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-297 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #209 | FUEL CELL EHT #209 | FUEL CELL AREA | EHT #210 | FUEL CELL EHT #210 | - | [21 empty] | L | EHT210 | 10 | L-EHT210-10 | EHT210 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X
X | 167 | L-SOFC301-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 81 | 24 | 452.39 | K-PC-421 | 41 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | K-TF-464 K-TF-127 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-110; ROUTING PATH 4: K-TF-104; ROUTING PATH 5: K-TF-103; ROUTING PATH 6: K-TF-102 |  |  | L | SOFC301 | 01 | L-SOFC301-01 | SOFC301 | 0.6/1kV FR-CV 1C-185㎟-P
X | 168 | L-SOFC301-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 81 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | K-TF-464 K-TF-127 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-110; ROUTING PATH 4: K-TF-104; ROUTING PATH 5: K-TF-103; ROUTING PATH 6: K-TF-102 |  |  | L | SOFC301 | 02 | L-SOFC301-02 | SOFC301 | 0.6/1kV FR-CV 1C-185㎟-P
X | 169 | L-SOFC301-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 81 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | K-TF-464 K-TF-127 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-110; ROUTING PATH 4: K-TF-104; ROUTING PATH 5: K-TF-103; ROUTING PATH 6: K-TF-102 |  |  | L | SOFC301 | 03 | L-SOFC301-03 | SOFC301 | 0.6/1kV FR-CV 1C-185㎟-P
X | 170 | L-SOFC301-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 81 | 24 | 452.39 | K-PC-422 | 41 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | K-TF-464 K-TF-127 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-110; ROUTING PATH 4: K-TF-104; ROUTING PATH 5: K-TF-103; ROUTING PATH 6: K-TF-102 |  |  | L | SOFC301 | 04 | L-SOFC301-04 | SOFC301 | 0.6/1kV FR-CV 1C-185㎟-P
X | 171 | L-SOFC301-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 81 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | K-TF-464 K-TF-127 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-110; ROUTING PATH 4: K-TF-104; ROUTING PATH 5: K-TF-103; ROUTING PATH 6: K-TF-102 |  |  | L | SOFC301 | 05 | L-SOFC301-05 | SOFC301 | 0.6/1kV FR-CV 1C-185㎟-P
X | 172 | L-SOFC301-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 81 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | K-TF-464 K-TF-127 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-127; ROUTING PATH 3: K-TF-110; ROUTING PATH 4: K-TF-104; ROUTING PATH 5: K-TF-103; ROUTING PATH 6: K-TF-102 |  |  | L | SOFC301 | 06 | L-SOFC301-06 | SOFC301 | 0.6/1kV FR-CV 1C-185㎟-P
X | 173 | L-SOFC302-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 76 | 24 | 452.39 | K-PC-011 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | K-TF-464 K-TF-227 K-TF-220 K-TF-217 K-TF-212 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-212 |  |  | L | SOFC302 | 01 | L-SOFC302-01 | SOFC302 | 0.6/1kV FR-CV 1C-185㎟-P
X | 174 | L-SOFC302-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 76 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | K-TF-464 K-TF-227 K-TF-220 K-TF-217 K-TF-212 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-212 |  |  | L | SOFC302 | 02 | L-SOFC302-02 | SOFC302 | 0.6/1kV FR-CV 1C-185㎟-P
X | 175 | L-SOFC302-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 76 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | K-TF-464 K-TF-227 K-TF-220 K-TF-217 K-TF-212 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-212 |  |  | L | SOFC302 | 03 | L-SOFC302-03 | SOFC302 | 0.6/1kV FR-CV 1C-185㎟-P
X | 176 | L-SOFC302-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 76 | 24 | 452.39 | K-PC-012 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | K-TF-464 K-TF-227 K-TF-220 K-TF-217 K-TF-212 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-212 |  |  | L | SOFC302 | 04 | L-SOFC302-04 | SOFC302 | 0.6/1kV FR-CV 1C-185㎟-P
X | 177 | L-SOFC302-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 76 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | K-TF-464 K-TF-227 K-TF-220 K-TF-217 K-TF-212 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-212 |  |  | L | SOFC302 | 05 | L-SOFC302-05 | SOFC302 | 0.6/1kV FR-CV 1C-185㎟-P
X | 178 | L-SOFC302-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 76 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | K-TF-464 K-TF-227 K-TF-220 K-TF-217 K-TF-212 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-212 |  |  | L | SOFC302 | 06 | L-SOFC302-06 | SOFC302 | 0.6/1kV FR-CV 1C-185㎟-P
X | 179 | L-SOFC303-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 73 | 24 | 452.39 | K-PC-063 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC303 | 01 | L-SOFC303-01 | SOFC303 | 0.6/1kV FR-CV 1C-185㎟-P
X | 180 | L-SOFC303-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 73 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC303 | 02 | L-SOFC303-02 | SOFC303 | 0.6/1kV FR-CV 1C-185㎟-P
X | 181 | L-SOFC303-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 73 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC303 | 03 | L-SOFC303-03 | SOFC303 | 0.6/1kV FR-CV 1C-185㎟-P
X | 182 | L-SOFC303-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 73 | 24 | 452.39 | K-PC-064 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC303 | 04 | L-SOFC303-04 | SOFC303 | 0.6/1kV FR-CV 1C-185㎟-P
X | 183 | L-SOFC303-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 73 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC303 | 05 | L-SOFC303-05 | SOFC303 | 0.6/1kV FR-CV 1C-185㎟-P
X | 184 | L-SOFC303-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 73 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC303 | 06 | L-SOFC303-06 | SOFC303 | 0.6/1kV FR-CV 1C-185㎟-P
X | 185 | L-SOFC304-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 | K-PC-102 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC304 | 01 | L-SOFC304-01 | SOFC304 | 0.6/1kV FR-CV 1C-185㎟-P
X | 186 | L-SOFC304-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC304 | 02 | L-SOFC304-02 | SOFC304 | 0.6/1kV FR-CV 1C-185㎟-P
X | 187 | L-SOFC304-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC304 | 03 | L-SOFC304-03 | SOFC304 | 0.6/1kV FR-CV 1C-185㎟-P
X | 188 | L-SOFC304-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 | K-PC-103 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC304 | 04 | L-SOFC304-04 | SOFC304 | 0.6/1kV FR-CV 1C-185㎟-P
X | 189 | L-SOFC304-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC304 | 05 | L-SOFC304-05 | SOFC304 | 0.6/1kV FR-CV 1C-185㎟-P
X | 190 | L-SOFC304-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC304 | 06 | L-SOFC304-06 | SOFC304 | 0.6/1kV FR-CV 1C-185㎟-P
X | 191 | L-SOFC305-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 | K-PC-144 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC305 | 01 | L-SOFC305-01 | SOFC305 | 0.6/1kV FR-CV 1C-185㎟-P
X | 192 | L-SOFC305-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC305 | 02 | L-SOFC305-02 | SOFC305 | 0.6/1kV FR-CV 1C-185㎟-P
X | 193 | L-SOFC305-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC305 | 03 | L-SOFC305-03 | SOFC305 | 0.6/1kV FR-CV 1C-185㎟-P
X | 194 | L-SOFC305-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 | K-PC-145 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC305 | 04 | L-SOFC305-04 | SOFC305 | 0.6/1kV FR-CV 1C-185㎟-P
X | 195 | L-SOFC305-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC305 | 05 | L-SOFC305-05 | SOFC305 | 0.6/1kV FR-CV 1C-185㎟-P
X | 196 | L-SOFC305-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | K-TF-464 K-TF-227 K-TF-220 K-TF-219 | ROUTING PATH 1: K-TF-464; ROUTING PATH 2: K-TF-227; ROUTING PATH 3: K-TF-220; ROUTING PATH 4: K-TF-219 |  |  | L | SOFC305 | 06 | L-SOFC305-06 | SOFC305 | 0.6/1kV FR-CV 1C-185㎟-P
X | 197 | L-SOFC306-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 | K-PC-211 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC306 | 01 | L-SOFC306-01 | SOFC306 | 0.6/1kV FR-CV 1C-185㎟-P
X | 198 | L-SOFC306-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC306 | 02 | L-SOFC306-02 | SOFC306 | 0.6/1kV FR-CV 1C-185㎟-P
X | 199 | L-SOFC306-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC306 | 03 | L-SOFC306-03 | SOFC306 | 0.6/1kV FR-CV 1C-185㎟-P
X | 200 | L-SOFC306-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 | K-PC-212 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC306 | 04 | L-SOFC306-04 | SOFC306 | 0.6/1kV FR-CV 1C-185㎟-P
X | 201 | L-SOFC306-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC306 | 05 | L-SOFC306-05 | SOFC306 | 0.6/1kV FR-CV 1C-185㎟-P
X | 202 | L-SOFC306-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC306 | 06 | L-SOFC306-06 | SOFC306 | 0.6/1kV FR-CV 1C-185㎟-P
X | 203 | L-SOFC307-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 | K-PC-253 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC307 | 01 | L-SOFC307-01 | SOFC307 | 0.6/1kV FR-CV 1C-185㎟-P
X | 204 | L-SOFC307-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC307 | 02 | L-SOFC307-02 | SOFC307 | 0.6/1kV FR-CV 1C-185㎟-P
X | 205 | L-SOFC307-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC307 | 03 | L-SOFC307-03 | SOFC307 | 0.6/1kV FR-CV 1C-185㎟-P
X | 206 | L-SOFC307-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 | K-PC-254 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC307 | 04 | L-SOFC307-04 | SOFC307 | 0.6/1kV FR-CV 1C-185㎟-P
X | 207 | L-SOFC307-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC307 | 05 | L-SOFC307-05 | SOFC307 | 0.6/1kV FR-CV 1C-185㎟-P
X | 208 | L-SOFC307-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 72 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC307 | 06 | L-SOFC307-06 | SOFC307 | 0.6/1kV FR-CV 1C-185㎟-P
X | 209 | L-SOFC308-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 | K-PC-291 | 39 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC308 | 01 | L-SOFC308-01 | SOFC308 | 0.6/1kV FR-CV 1C-185㎟-P
X | 210 | L-SOFC308-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC308 | 02 | L-SOFC308-02 | SOFC308 | 0.6/1kV FR-CV 1C-185㎟-P
X | 211 | L-SOFC308-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC308 | 03 | L-SOFC308-03 | SOFC308 | 0.6/1kV FR-CV 1C-185㎟-P
X | 212 | L-SOFC308-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 | K-PC-292 | 39 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC308 | 04 | L-SOFC308-04 | SOFC308 | 0.6/1kV FR-CV 1C-185㎟-P
X | 213 | L-SOFC308-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC308 | 05 | L-SOFC308-05 | SOFC308 | 0.6/1kV FR-CV 1C-185㎟-P
X | 214 | L-SOFC308-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC308 | 06 | L-SOFC308-06 | SOFC308 | 0.6/1kV FR-CV 1C-185㎟-P
X | 215 | L-SOFC309-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 79 | 24 | 452.39 | K-PC-343 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC309 | 01 | L-SOFC309-01 | SOFC309 | 0.6/1kV FR-CV 1C-185㎟-P
X | 216 | L-SOFC309-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 79 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC309 | 02 | L-SOFC309-02 | SOFC309 | 0.6/1kV FR-CV 1C-185㎟-P
X | 217 | L-SOFC309-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 79 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC309 | 03 | L-SOFC309-03 | SOFC309 | 0.6/1kV FR-CV 1C-185㎟-P
X | 218 | L-SOFC309-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 79 | 24 | 452.39 | K-PC-344 | 38 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC309 | 04 | L-SOFC309-04 | SOFC309 | 0.6/1kV FR-CV 1C-185㎟-P
X | 219 | L-SOFC309-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 79 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC309 | 05 | L-SOFC309-05 | SOFC309 | 0.6/1kV FR-CV 1C-185㎟-P
X | 220 | L-SOFC309-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 79 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | K-TF-463 K-TF-226 K-TF-237 K-TF-234 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-226; ROUTING PATH 3: K-TF-237; ROUTING PATH 4: K-TF-234 |  |  | L | SOFC309 | 06 | L-SOFC309-06 | SOFC309 | 0.6/1kV FR-CV 1C-185㎟-P
X | 221 | L-SOFC310-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 83 | 24 | 452.39 | K-PC-511 | 43 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | K-TF-463 K-TF-126 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-126; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC310 | 01 | L-SOFC310-01 | SOFC310 | 0.6/1kV FR-CV 1C-185㎟-P
X | 222 | L-SOFC310-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 83 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | K-TF-463 K-TF-126 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-126; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC310 | 02 | L-SOFC310-02 | SOFC310 | 0.6/1kV FR-CV 1C-185㎟-P
X | 223 | L-SOFC310-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 83 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | K-TF-463 K-TF-126 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-126; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC310 | 03 | L-SOFC310-03 | SOFC310 | 0.6/1kV FR-CV 1C-185㎟-P
X | 224 | L-SOFC310-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 83 | 24 | 452.39 | K-PC-512 | 43 | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | K-TF-463 K-TF-126 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-126; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC310 | 04 | L-SOFC310-04 | SOFC310 | 0.6/1kV FR-CV 1C-185㎟-P
X | 225 | L-SOFC310-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 83 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | K-TF-463 K-TF-126 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-126; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC310 | 05 | L-SOFC310-05 | SOFC310 | 0.6/1kV FR-CV 1C-185㎟-P
X | 226 | L-SOFC310-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 83 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-302 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | K-TF-463 K-TF-126 K-TF-137 K-TF-134 | ROUTING PATH 1: K-TF-463; ROUTING PATH 2: K-TF-126; ROUTING PATH 3: K-TF-137; ROUTING PATH 4: K-TF-134 |  |  | L | SOFC310 | 06 | L-SOFC310-06 | SOFC310 | 0.6/1kV FR-CV 1C-185㎟-P
X | 227 | L-WDM301-01 | P | 0.6/1kV | FR-CV | 2C | 10 | 75 | 17 | 226.99 | K-PB-432 | 45 | 0.12 | 1.2 | F | 전기실 | EL-LV-303 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #301 | WATER DISTRIBUTION MODULE #301 | K-TF-226 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-226; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | WDM301 | 01 | L-WDM301-01 | WDM301 | 0.6/1kV FR-CV 2C-10㎟-P
X | 228 | L-WDM302-02 | P | 0.6/1kV | FR-CV | 2C | 10 | 77 | 17 | 226.99 | K-PB-433 | 44 | 0.12 | 1.2 | F | 전기실 | EL-LV-303 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #302 | WATER DISTRIBUTION MODULE #302 | K-TF-226 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-226; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | WDM302 | 02 | L-WDM302-02 | WDM302 | 0.6/1kV FR-CV 2C-10㎟-P
X | 229 | L-TC301-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 73 | 22 | 380.14 | K-PB-423 | 42 | 0.12 | 2.04 | F | 전기실 | EL-LV-303 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | TC #301 | TELE CABINET #301 | K-TF-226 K-TF-210 K-TF-204 K-TF-203 K-TF-202 | ROUTING PATH 1: K-TF-226; ROUTING PATH 2: K-TF-210; ROUTING PATH 3: K-TF-204; ROUTING PATH 4: K-TF-203; ROUTING PATH 5: K-TF-202 |  |  | L | TC301 | 01 | L-TC301-01 | TC301 | 0.6/1kV FR-CV 2C-25㎟-P
O | 230 | L-EHT304-04 | P | 0.6/1kV | FR-CV | 2C | 6 | 69 | 14 | 153.94 | K-PB-101 | 38 | 0.12 | 0.5 | F | 전기실 | EL-LV-303 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #304 | FUEL CELL EHT #304 | K-TF-126 K-TF-120 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-126; ROUTING PATH 2: K-TF-120; ROUTING PATH 3: K-TF-116; ROUTING PATH 4: K-TF-112 |  |  | L | EHT304 | 04 | L-EHT304-04 | EHT304 | 0.6/1kV FR-CV 2C-6㎟-P
X | 231 | L-EHT303-03 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-125 | 8 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #304 | FUEL CELL EHT #304 | FUEL CELL AREA | EHT #303 | FUEL CELL EHT #303 | - | [21 empty] | L | EHT303 | 03 | L-EHT303-03 | EHT303 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 232 | L-EHT302-02 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-126 | 10 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #303 | FUEL CELL EHT #303 | FUEL CELL AREA | EHT #302 | FUEL CELL EHT #302 | - | [21 empty] | L | EHT302 | 02 | L-EHT302-02 | EHT302 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 233 | L-EHT301-01 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-127 | 8 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #302 | FUEL CELL EHT #302 | FUEL CELL AREA | EHT #301 | FUEL CELL EHT #301 | - | [21 empty] | L | EHT301 | 01 | L-EHT301-01 | EHT301 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
O | 234 | L-EHT305-05 | P | 0.6/1kV | FR-CV | 2C | 6 | 66 | 14 | 153.94 | K-PB-151 | 38 | 0.12 | 0.375 | F | 전기실 | EL-LV-303 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #305 | FUEL CELL EHT #305 | K-TF-126 K-TF-120 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-126; ROUTING PATH 2: K-TF-120; ROUTING PATH 3: K-TF-116; ROUTING PATH 4: K-TF-112 |  |  | L | EHT305 | 05 | L-EHT305-05 | EHT305 | 0.6/1kV FR-CV 2C-6㎟-P
X | 235 | L-EHT306-06 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-155 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #305 | FUEL CELL EHT #305 | FUEL CELL AREA | EHT #306 | FUEL CELL EHT #306 | - | [21 empty] | L | EHT306 | 06 | L-EHT306-06 | EHT306 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 236 | L-EHT307-07 | P | 0.6/1kV | FR-CV | 2C | 6 | 11 | 14 | 153.94 | K-PA-156 | 11 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #306 | FUEL CELL EHT #306 | FUEL CELL AREA | EHT #307 | FUEL CELL EHT #307 | - | [21 empty] | L | EHT307 | 07 | L-EHT307-07 | EHT307 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 237 | L-EHT308-08 | P | 0.6/1kV | FR-CV | 2C | 6 | 78 | 14 | 153.94 | K-PB-304 | 39 | 0.12 | 0.375 | F | 전기실 | EL-LV-303 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #308 | FUEL CELL EHT #308 | K-TF-127 K-TF-137 K-TF-134 K-PC-564 | ROUTING PATH 1: K-TF-127; ROUTING PATH 2: K-TF-137; ROUTING PATH 3: K-TF-134; ROUTING PATH 4: K-PC-564 |  |  | L | EHT308 | 08 | L-EHT308-08 | EHT308 | 0.6/1kV FR-CV 2C-6㎟-P
X | 238 | L-EHT309-09 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-305 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #308 | FUEL CELL EHT #308 | FUEL CELL AREA | EHT #309 | FUEL CELL EHT #309 | - | [21 empty] | L | EHT309 | 09 | L-EHT309-09 | EHT309 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 239 | L-EHT310-10 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-306 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #309 | FUEL CELL EHT #309 | FUEL CELL AREA | EHT #310 | FUEL CELL EHT #310 | - | [21 empty] | L | EHT310 | 10 | L-EHT310-10 | EHT310 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X
X | 240 | L-SOFC401-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 85 | 24 | 452.39 | K-PC-651 | 48 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC401 | 01 | L-SOFC401-01 | SOFC401 | 0.6/1kV FR-CV 1C-185㎟-P
X | 241 | L-SOFC401-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 85 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC401 | 02 | L-SOFC401-02 | SOFC401 | 0.6/1kV FR-CV 1C-185㎟-P
X | 242 | L-SOFC401-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 85 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC401 | 03 | L-SOFC401-03 | SOFC401 | 0.6/1kV FR-CV 1C-185㎟-P
X | 243 | L-SOFC401-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 85 | 24 | 452.39 | K-PC-652 | 48 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC401 | 04 | L-SOFC401-04 | SOFC401 | 0.6/1kV FR-CV 1C-185㎟-P
X | 244 | L-SOFC401-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 85 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC401 | 05 | L-SOFC401-05 | SOFC401 | 0.6/1kV FR-CV 1C-185㎟-P
X | 245 | L-SOFC401-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 85 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC401 | 06 | L-SOFC401-06 | SOFC401 | 0.6/1kV FR-CV 1C-185㎟-P
X | 246 | L-SOFC402-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 80 | 24 | 452.39 | K-PC-023 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC402 | 01 | L-SOFC402-01 | SOFC402 | 0.6/1kV FR-CV 1C-185㎟-P
X | 247 | L-SOFC402-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 80 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC402 | 02 | L-SOFC402-02 | SOFC402 | 0.6/1kV FR-CV 1C-185㎟-P
X | 248 | L-SOFC402-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 80 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC402 | 03 | L-SOFC402-03 | SOFC402 | 0.6/1kV FR-CV 1C-185㎟-P
X | 249 | L-SOFC402-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 80 | 24 | 452.39 | K-PC-024 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC402 | 04 | L-SOFC402-04 | SOFC402 | 0.6/1kV FR-CV 1C-185㎟-P
X | 250 | L-SOFC402-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 80 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC402 | 05 | L-SOFC402-05 | SOFC402 | 0.6/1kV FR-CV 1C-185㎟-P
X | 251 | L-SOFC402-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 80 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC402 | 06 | L-SOFC402-06 | SOFC402 | 0.6/1kV FR-CV 1C-185㎟-P
X | 252 | L-SOFC403-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 78 | 24 | 452.39 | K-PC-071 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC403 | 01 | L-SOFC403-01 | SOFC403 | 0.6/1kV FR-CV 1C-185㎟-P
X | 253 | L-SOFC403-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 78 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC403 | 02 | L-SOFC403-02 | SOFC403 | 0.6/1kV FR-CV 1C-185㎟-P
X | 254 | L-SOFC403-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 78 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC403 | 03 | L-SOFC403-03 | SOFC403 | 0.6/1kV FR-CV 1C-185㎟-P
X | 255 | L-SOFC403-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 78 | 24 | 452.39 | K-PC-072 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC403 | 04 | L-SOFC403-04 | SOFC403 | 0.6/1kV FR-CV 1C-185㎟-P
X | 256 | L-SOFC403-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 78 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC403 | 05 | L-SOFC403-05 | SOFC403 | 0.6/1kV FR-CV 1C-185㎟-P
X | 257 | L-SOFC403-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 78 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | K-TF-467 K-TF-146 K-TF-126 K-TF-110 K-TF-104 K-TF-103 K-TF-102 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-110; ROUTING PATH 5: K-TF-104; ROUTING PATH 6: K-TF-103; ROUTING PATH 7: K-TF-102 |  |  | L | SOFC403 | 06 | L-SOFC403-06 | SOFC403 | 0.6/1kV FR-CV 1C-185㎟-P
X | 258 | L-SOFC404-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 | K-PC-114 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC404 | 01 | L-SOFC404-01 | SOFC404 | 0.6/1kV FR-CV 1C-185㎟-P
X | 259 | L-SOFC404-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC404 | 02 | L-SOFC404-02 | SOFC404 | 0.6/1kV FR-CV 1C-185㎟-P
X | 260 | L-SOFC404-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC404 | 03 | L-SOFC404-03 | SOFC404 | 0.6/1kV FR-CV 1C-185㎟-P
X | 261 | L-SOFC404-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 | K-PC-115 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC404 | 04 | L-SOFC404-04 | SOFC404 | 0.6/1kV FR-CV 1C-185㎟-P
X | 262 | L-SOFC404-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC404 | 05 | L-SOFC404-05 | SOFC404 | 0.6/1kV FR-CV 1C-185㎟-P
X | 263 | L-SOFC404-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 74 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC404 | 06 | L-SOFC404-06 | SOFC404 | 0.6/1kV FR-CV 1C-185㎟-P
X | 264 | L-SOFC405-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 70 | 24 | 452.39 | K-PC-152 | 47 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC405 | 01 | L-SOFC405-01 | SOFC405 | 0.6/1kV FR-CV 1C-185㎟-P
X | 265 | L-SOFC405-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 70 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC405 | 02 | L-SOFC405-02 | SOFC405 | 0.6/1kV FR-CV 1C-185㎟-P
X | 266 | L-SOFC405-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 70 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC405 | 03 | L-SOFC405-03 | SOFC405 | 0.6/1kV FR-CV 1C-185㎟-P
X | 267 | L-SOFC405-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 70 | 24 | 452.39 | K-PC-153 | 47 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC405 | 04 | L-SOFC405-04 | SOFC405 | 0.6/1kV FR-CV 1C-185㎟-P
X | 268 | L-SOFC405-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 70 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC405 | 05 | L-SOFC405-05 | SOFC405 | 0.6/1kV FR-CV 1C-185㎟-P
X | 269 | L-SOFC405-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 70 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | K-TF-467 K-TF-146 K-TF-126 K-TF-120 K-TF-119 | ROUTING PATH 1: K-TF-467; ROUTING PATH 2: K-TF-146; ROUTING PATH 3: K-TF-126; ROUTING PATH 4: K-TF-120; ROUTING PATH 5: K-TF-119 |  |  | L | SOFC405 | 06 | L-SOFC405-06 | SOFC405 | 0.6/1kV FR-CV 1C-185㎟-P
X | 270 | L-SOFC406-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 66 | 24 | 452.39 | K-PC-223 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC406 | 01 | L-SOFC406-01 | SOFC406 | 0.6/1kV FR-CV 1C-185㎟-P
X | 271 | L-SOFC406-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 66 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC406 | 02 | L-SOFC406-02 | SOFC406 | 0.6/1kV FR-CV 1C-185㎟-P
X | 272 | L-SOFC406-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 66 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC406 | 03 | L-SOFC406-03 | SOFC406 | 0.6/1kV FR-CV 1C-185㎟-P
X | 273 | L-SOFC406-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 66 | 24 | 452.39 | K-PC-224 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC406 | 04 | L-SOFC406-04 | SOFC406 | 0.6/1kV FR-CV 1C-185㎟-P
X | 274 | L-SOFC406-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 66 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC406 | 05 | L-SOFC406-05 | SOFC406 | 0.6/1kV FR-CV 1C-185㎟-P
X | 275 | L-SOFC406-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 66 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC406 | 06 | L-SOFC406-06 | SOFC406 | 0.6/1kV FR-CV 1C-185㎟-P
X | 276 | L-SOFC407-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 | K-PC-261 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC407 | 01 | L-SOFC407-01 | SOFC407 | 0.6/1kV FR-CV 1C-185㎟-P
X | 277 | L-SOFC407-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC407 | 02 | L-SOFC407-02 | SOFC407 | 0.6/1kV FR-CV 1C-185㎟-P
X | 278 | L-SOFC407-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC407 | 03 | L-SOFC407-03 | SOFC407 | 0.6/1kV FR-CV 1C-185㎟-P
X | 279 | L-SOFC407-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 | K-PC-262 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC407 | 04 | L-SOFC407-04 | SOFC407 | 0.6/1kV FR-CV 1C-185㎟-P
X | 280 | L-SOFC407-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC407 | 05 | L-SOFC407-05 | SOFC407 | 0.6/1kV FR-CV 1C-185㎟-P
X | 281 | L-SOFC407-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 68 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | K-TF-468 K-TF-250 K-TF-249 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-250; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC407 | 06 | L-SOFC407-06 | SOFC407 | 0.6/1kV FR-CV 1C-185㎟-P
X | 282 | L-SOFC408-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 | K-PC-302 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC408 | 01 | L-SOFC408-01 | SOFC408 | 0.6/1kV FR-CV 1C-185㎟-P
X | 283 | L-SOFC408-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC408 | 02 | L-SOFC408-02 | SOFC408 | 0.6/1kV FR-CV 1C-185㎟-P
X | 284 | L-SOFC408-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC408 | 03 | L-SOFC408-03 | SOFC408 | 0.6/1kV FR-CV 1C-185㎟-P
X | 285 | L-SOFC408-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 | K-PC-303 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC408 | 04 | L-SOFC408-04 | SOFC408 | 0.6/1kV FR-CV 1C-185㎟-P
X | 286 | L-SOFC408-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC408 | 05 | L-SOFC408-05 | SOFC408 | 0.6/1kV FR-CV 1C-185㎟-P
X | 287 | L-SOFC408-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 69 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC408 | 06 | L-SOFC408-06 | SOFC408 | 0.6/1kV FR-CV 1C-185㎟-P
X | 288 | L-SOFC409-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 71 | 24 | 452.39 | K-PC-351 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC409 | 01 | L-SOFC409-01 | SOFC409 | 0.6/1kV FR-CV 1C-185㎟-P
X | 289 | L-SOFC409-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 71 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC409 | 02 | L-SOFC409-02 | SOFC409 | 0.6/1kV FR-CV 1C-185㎟-P
X | 290 | L-SOFC409-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 71 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC409 | 03 | L-SOFC409-03 | SOFC409 | 0.6/1kV FR-CV 1C-185㎟-P
X | 291 | L-SOFC409-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 71 | 24 | 452.39 | K-PC-352 | 46 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC409 | 04 | L-SOFC409-04 | SOFC409 | 0.6/1kV FR-CV 1C-185㎟-P
X | 292 | L-SOFC409-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 71 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC409 | 05 | L-SOFC409-05 | SOFC409 | 0.6/1kV FR-CV 1C-185㎟-P
X | 293 | L-SOFC409-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 71 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC409 | 06 | L-SOFC409-06 | SOFC409 | 0.6/1kV FR-CV 1C-185㎟-P
X | 294 | L-SOFC410-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 75 | 24 | 452.39 | K-PC-723 | 49 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC410 | 01 | L-SOFC410-01 | SOFC410 | 0.6/1kV FR-CV 1C-185㎟-P
X | 295 | L-SOFC410-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 75 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC410 | 02 | L-SOFC410-02 | SOFC410 | 0.6/1kV FR-CV 1C-185㎟-P
X | 296 | L-SOFC410-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 75 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC410 | 03 | L-SOFC410-03 | SOFC410 | 0.6/1kV FR-CV 1C-185㎟-P
X | 297 | L-SOFC410-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 75 | 24 | 452.39 | K-PC-724 | 49 | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC410 | 04 | L-SOFC410-04 | SOFC410 | 0.6/1kV FR-CV 1C-185㎟-P
X | 298 | L-SOFC410-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 75 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC410 | 05 | L-SOFC410-05 | SOFC410 | 0.6/1kV FR-CV 1C-185㎟-P
X | 299 | L-SOFC410-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 75 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-402 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | K-TF-468 K-TF-150 K-TF-149 | ROUTING PATH 1: K-TF-468; ROUTING PATH 2: K-TF-150; ROUTING PATH 3: K-TF-149 |  |  | L | SOFC410 | 06 | L-SOFC410-06 | SOFC410 | 0.6/1kV FR-CV 1C-185㎟-P
X | 300 | L-WDM401-01 | P | 0.6/1kV | FR-CV | 2C | 10 | 81 | 17 | 226.99 | K-PB-662 | 9 | 0.12 | 1.2 | F | 전기실 | EL-LV-403 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #401 | WATER DISTRIBUTION MODULE #401 | K-TF-146 K-TF-137 K-TF-136 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-146; ROUTING PATH 2: K-TF-137; ROUTING PATH 3: K-TF-136; ROUTING PATH 4: K-TF-124; ROUTING PATH 5: K-TF-117; ROUTING PATH 6: K-TF-108; ROUTING PATH 7: K-TF-102 |  |  | L | WDM401 | 01 | L-WDM401-01 | WDM401 | 0.6/1kV FR-CV 2C-10㎟-P
X | 301 | L-WDM402-02 | P | 0.6/1kV | FR-CV | 2C | 10 | 83 | 17 | 226.99 | K-PB-663 | 8 | 0.12 | 1.2 | F | 전기실 | EL-LV-403 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #402 | WATER DISTRIBUTION MODULE #402 | K-TF-146 K-TF-137 K-TF-136 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-146; ROUTING PATH 2: K-TF-137; ROUTING PATH 3: K-TF-136; ROUTING PATH 4: K-TF-124; ROUTING PATH 5: K-TF-117; ROUTING PATH 6: K-TF-108; ROUTING PATH 7: K-TF-102 |  |  | L | WDM402 | 02 | L-WDM402-02 | WDM402 | 0.6/1kV FR-CV 2C-10㎟-P
X | 302 | L-TC401-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 79 | 22 | 380.14 | K-PB-653 | 6 | 0.12 | 2.04 | F | 전기실 | EL-LV-403 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | TC #401 | TELE CABINET #401 | K-TF-146 K-TF-137 K-TF-136 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-146; ROUTING PATH 2: K-TF-137; ROUTING PATH 3: K-TF-136; ROUTING PATH 4: K-TF-124; ROUTING PATH 5: K-TF-117; ROUTING PATH 6: K-TF-108; ROUTING PATH 7: K-TF-102 |  |  | L | TC401 | 01 | L-TC401-01 | TC401 | 0.6/1kV FR-CV 2C-25㎟-P
O | 303 | L-EHT404-04 | P | 0.6/1kV | FR-CV | 2C | 6 | 72 | 14 | 153.94 | K-PB-113 | 46 | 0.12 | 0.5 | F | 전기실 | EL-LV-403 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #404 | FUEL CELL EHT #404 | K-TF-146 K-TF-137 K-TF-136 K-TF-124 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-146; ROUTING PATH 2: K-TF-137; ROUTING PATH 3: K-TF-136; ROUTING PATH 4: K-TF-124; ROUTING PATH 5: K-TF-116; ROUTING PATH 6: K-TF-112 |  |  | L | EHT404 | 04 | L-EHT404-04 | EHT404 | 0.6/1kV FR-CV 2C-6㎟-P
X | 304 | L-EHT403-03 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-116 | 8 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #404 | FUEL CELL EHT #404 | FUEL CELL AREA | EHT #403 | FUEL CELL EHT #403 | - | [21 empty] | L | EHT403 | 03 | L-EHT403-03 | EHT403 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 305 | L-EHT402-02 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-117 | 10 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #403 | FUEL CELL EHT #403 | FUEL CELL AREA | EHT #402 | FUEL CELL EHT #402 | - | [21 empty] | L | EHT402 | 02 | L-EHT402-02 | EHT402 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 306 | L-EHT401-01 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-118 | 8 | 0.12 | 0.5 | F | FUEL CELL AREA | EHT #402 | FUEL CELL EHT #402 | FUEL CELL AREA | EHT #401 | FUEL CELL EHT #401 | - | [21 empty] | L | EHT401 | 01 | L-EHT401-01 | EHT401 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
O | 307 | L-EHT405-05 | P | 0.6/1kV | FR-CV | 2C | 6 | 74 | 14 | 153.94 | K-PB-154 | 47 | 0.12 | 0.375 | F | 전기실 | EL-LV-403 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #405 | FUEL CELL EHT #405 | K-TF-146 K-TF-137 K-TF-136 K-TF-124 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-146; ROUTING PATH 2: K-TF-137; ROUTING PATH 3: K-TF-136; ROUTING PATH 4: K-TF-124; ROUTING PATH 5: K-TF-116; ROUTING PATH 6: K-TF-112 |  |  | L | EHT405 | 05 | L-EHT405-05 | EHT405 | 0.6/1kV FR-CV 2C-6㎟-P
X | 308 | L-EHT406-06 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-157 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #405 | FUEL CELL EHT #405 | FUEL CELL AREA | EHT #406 | FUEL CELL EHT #406 | - | [21 empty] | L | EHT406 | 06 | L-EHT406-06 | EHT406 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 309 | L-EHT407-07 | P | 0.6/1kV | FR-CV | 2C | 6 | 11 | 14 | 153.94 | K-PA-158 | 11 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #406 | FUEL CELL EHT #406 | FUEL CELL AREA | EHT #407 | FUEL CELL EHT #407 | - | [21 empty] | L | EHT407 | 07 | L-EHT407-07 | EHT407 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
O | 310 | L-EHT408-08 | P | 0.6/1kV | FR-CV | 2C | 6 | 71 | 14 | 153.94 | K-PB-301 | 46 | 0.12 | 0.375 | F | 전기실 | EL-LV-403 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #408 | FUEL CELL EHT #408 | K-TF-146 K-TF-137 K-TF-136 K-TF-124 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-146; ROUTING PATH 2: K-TF-137; ROUTING PATH 3: K-TF-136; ROUTING PATH 4: K-TF-124; ROUTING PATH 5: K-TF-116; ROUTING PATH 6: K-TF-112 |  |  | L | EHT408 | 08 | L-EHT408-08 | EHT408 | 0.6/1kV FR-CV 2C-6㎟-P
X | 311 | L-EHT409-09 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-307 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #408 | FUEL CELL EHT #408 | FUEL CELL AREA | EHT #409 | FUEL CELL EHT #409 | - | [21 empty] | L | EHT409 | 09 | L-EHT409-09 | EHT409 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 312 | L-EHT410-10 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-308 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #409 | FUEL CELL EHT #409 | FUEL CELL AREA | EHT #410 | FUEL CELL EHT #410 | - | [21 empty] | L | EHT410 | 10 | L-EHT410-10 | EHT410 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X
X | 313 | L-SOFC501-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 | K-PC-021 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC501 | 01 | L-SOFC501-01 | SOFC501 | 0.6/1kV FR-CV 1C-185㎟-P
X | 314 | L-SOFC501-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC501 | 02 | L-SOFC501-02 | SOFC501 | 0.6/1kV FR-CV 1C-185㎟-P
X | 315 | L-SOFC501-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC501 | 03 | L-SOFC501-03 | SOFC501 | 0.6/1kV FR-CV 1C-185㎟-P
X | 316 | L-SOFC501-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 | K-PC-022 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC501 | 04 | L-SOFC501-04 | SOFC501 | 0.6/1kV FR-CV 1C-185㎟-P
X | 317 | L-SOFC501-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC501 | 05 | L-SOFC501-05 | SOFC501 | 0.6/1kV FR-CV 1C-185㎟-P
X | 318 | L-SOFC501-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC501 | 06 | L-SOFC501-06 | SOFC501 | 0.6/1kV FR-CV 1C-185㎟-P
X | 319 | L-SOFC502-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 110 | 24 | 452.39 | K-PC-073 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC502 | 01 | L-SOFC502-01 | SOFC502 | 0.6/1kV FR-CV 1C-185㎟-P
X | 320 | L-SOFC502-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 110 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC502 | 02 | L-SOFC502-02 | SOFC502 | 0.6/1kV FR-CV 1C-185㎟-P
X | 321 | L-SOFC502-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 110 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC502 | 03 | L-SOFC502-03 | SOFC502 | 0.6/1kV FR-CV 1C-185㎟-P
X | 322 | L-SOFC502-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 110 | 24 | 452.39 | K-PC-074 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC502 | 04 | L-SOFC502-04 | SOFC502 | 0.6/1kV FR-CV 1C-185㎟-P
X | 323 | L-SOFC502-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 110 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC502 | 05 | L-SOFC502-05 | SOFC502 | 0.6/1kV FR-CV 1C-185㎟-P
X | 324 | L-SOFC502-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 110 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | K-TF-458 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-117; ROUTING PATH 4: K-TF-108; ROUTING PATH 5: K-TF-102 |  |  | L | SOFC502 | 06 | L-SOFC502-06 | SOFC502 | 0.6/1kV FR-CV 1C-185㎟-P
X | 325 | L-SOFC503-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 | K-PC-111 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | K-TF-457 K-TF-223 K-TF-219 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC503 | 01 | L-SOFC503-01 | SOFC503 | 0.6/1kV FR-CV 1C-185㎟-P
X | 326 | L-SOFC503-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | K-TF-457 K-TF-223 K-TF-219 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC503 | 02 | L-SOFC503-02 | SOFC503 | 0.6/1kV FR-CV 1C-185㎟-P
X | 327 | L-SOFC503-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | K-TF-457 K-TF-223 K-TF-219 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC503 | 03 | L-SOFC503-03 | SOFC503 | 0.6/1kV FR-CV 1C-185㎟-P
X | 328 | L-SOFC503-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 | K-PC-112 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | K-TF-457 K-TF-223 K-TF-219 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC503 | 04 | L-SOFC503-04 | SOFC503 | 0.6/1kV FR-CV 1C-185㎟-P
X | 329 | L-SOFC503-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | K-TF-457 K-TF-223 K-TF-219 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC503 | 05 | L-SOFC503-05 | SOFC503 | 0.6/1kV FR-CV 1C-185㎟-P
X | 330 | L-SOFC503-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 105 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | K-TF-457 K-TF-223 K-TF-219 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-219 |  |  | L | SOFC503 | 06 | L-SOFC503-06 | SOFC503 | 0.6/1kV FR-CV 1C-185㎟-P
X | 331 | L-SOFC504-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 101 | 24 | 452.39 | K-PC-161 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | K-TF-457 K-TF-123 K-TF-119 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-119 |  |  | L | SOFC504 | 01 | L-SOFC504-01 | SOFC504 | 0.6/1kV FR-CV 1C-185㎟-P
X | 332 | L-SOFC504-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 101 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | K-TF-457 K-TF-123 K-TF-119 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-119 |  |  | L | SOFC504 | 02 | L-SOFC504-02 | SOFC504 | 0.6/1kV FR-CV 1C-185㎟-P
X | 333 | L-SOFC504-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 101 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | K-TF-457 K-TF-123 K-TF-119 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-119 |  |  | L | SOFC504 | 03 | L-SOFC504-03 | SOFC504 | 0.6/1kV FR-CV 1C-185㎟-P
X | 334 | L-SOFC504-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 101 | 24 | 452.39 | K-PC-162 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | K-TF-457 K-TF-123 K-TF-119 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-119 |  |  | L | SOFC504 | 04 | L-SOFC504-04 | SOFC504 | 0.6/1kV FR-CV 1C-185㎟-P
X | 335 | L-SOFC504-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 101 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | K-TF-457 K-TF-123 K-TF-119 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-119 |  |  | L | SOFC504 | 05 | L-SOFC504-05 | SOFC504 | 0.6/1kV FR-CV 1C-185㎟-P
X | 336 | L-SOFC504-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 101 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | K-TF-457 K-TF-123 K-TF-119 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-119 |  |  | L | SOFC504 | 06 | L-SOFC504-06 | SOFC504 | 0.6/1kV FR-CV 1C-185㎟-P
X | 337 | L-SOFC505-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-221 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC505 | 01 | L-SOFC505-01 | SOFC505 | 0.6/1kV FR-CV 1C-185㎟-P
X | 338 | L-SOFC505-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC505 | 02 | L-SOFC505-02 | SOFC505 | 0.6/1kV FR-CV 1C-185㎟-P
X | 339 | L-SOFC505-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC505 | 03 | L-SOFC505-03 | SOFC505 | 0.6/1kV FR-CV 1C-185㎟-P
X | 340 | L-SOFC505-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-222 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC505 | 04 | L-SOFC505-04 | SOFC505 | 0.6/1kV FR-CV 1C-185㎟-P
X | 341 | L-SOFC505-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC505 | 05 | L-SOFC505-05 | SOFC505 | 0.6/1kV FR-CV 1C-185㎟-P
X | 342 | L-SOFC505-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC505 | 06 | L-SOFC505-06 | SOFC505 | 0.6/1kV FR-CV 1C-185㎟-P
X | 343 | L-SOFC506-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 94 | 24 | 452.39 | K-PC-263 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC506 | 01 | L-SOFC506-01 | SOFC506 | 0.6/1kV FR-CV 1C-185㎟-P
X | 344 | L-SOFC506-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 94 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC506 | 02 | L-SOFC506-02 | SOFC506 | 0.6/1kV FR-CV 1C-185㎟-P
X | 345 | L-SOFC506-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 94 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC506 | 03 | L-SOFC506-03 | SOFC506 | 0.6/1kV FR-CV 1C-185㎟-P
X | 346 | L-SOFC506-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 94 | 24 | 452.39 | K-PC-264 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC506 | 04 | L-SOFC506-04 | SOFC506 | 0.6/1kV FR-CV 1C-185㎟-P
X | 347 | L-SOFC506-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 94 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC506 | 05 | L-SOFC506-05 | SOFC506 | 0.6/1kV FR-CV 1C-185㎟-P
X | 348 | L-SOFC506-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 94 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC506 | 06 | L-SOFC506-06 | SOFC506 | 0.6/1kV FR-CV 1C-185㎟-P
X | 349 | L-SOFC507-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-313 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC507 | 01 | L-SOFC507-01 | SOFC507 | 0.6/1kV FR-CV 1C-185㎟-P
X | 350 | L-SOFC507-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC507 | 02 | L-SOFC507-02 | SOFC507 | 0.6/1kV FR-CV 1C-185㎟-P
X | 351 | L-SOFC507-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC507 | 03 | L-SOFC507-03 | SOFC507 | 0.6/1kV FR-CV 1C-185㎟-P
X | 352 | L-SOFC507-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-314 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC507 | 04 | L-SOFC507-04 | SOFC507 | 0.6/1kV FR-CV 1C-185㎟-P
X | 353 | L-SOFC507-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC507 | 05 | L-SOFC507-05 | SOFC507 | 0.6/1kV FR-CV 1C-185㎟-P
X | 354 | L-SOFC507-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | K-TF-457 K-TF-323 K-TF-322 | ROUTING PATH 1: K-TF-457; ROUTING PATH 2: K-TF-323; ROUTING PATH 3: K-TF-322 |  |  | L | SOFC507 | 06 | L-SOFC507-06 | SOFC507 | 0.6/1kV FR-CV 1C-185㎟-P
X | 355 | L-SOFC508-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 97 | 24 | 452.39 | K-PC-353 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC508 | 01 | L-SOFC508-01 | SOFC508 | 0.6/1kV FR-CV 1C-185㎟-P
X | 356 | L-SOFC508-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 97 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC508 | 02 | L-SOFC508-02 | SOFC508 | 0.6/1kV FR-CV 1C-185㎟-P
X | 357 | L-SOFC508-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 97 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC508 | 03 | L-SOFC508-03 | SOFC508 | 0.6/1kV FR-CV 1C-185㎟-P
X | 358 | L-SOFC508-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 97 | 24 | 452.39 | K-PC-354 | 63 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC508 | 04 | L-SOFC508-04 | SOFC508 | 0.6/1kV FR-CV 1C-185㎟-P
X | 359 | L-SOFC508-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 97 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC508 | 05 | L-SOFC508-05 | SOFC508 | 0.6/1kV FR-CV 1C-185㎟-P
X | 360 | L-SOFC508-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 97 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC508 | 06 | L-SOFC508-06 | SOFC508 | 0.6/1kV FR-CV 1C-185㎟-P
X | 361 | L-SOFC509-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 102 | 24 | 452.39 | K-PC-721 | 66 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC509 | 01 | L-SOFC509-01 | SOFC509 | 0.6/1kV FR-CV 1C-185㎟-P
X | 362 | L-SOFC509-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 102 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC509 | 02 | L-SOFC509-02 | SOFC509 | 0.6/1kV FR-CV 1C-185㎟-P
X | 363 | L-SOFC509-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 102 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC509 | 03 | L-SOFC509-03 | SOFC509 | 0.6/1kV FR-CV 1C-185㎟-P
X | 364 | L-SOFC509-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 102 | 24 | 452.39 | K-PC-722 | 66 | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC509 | 04 | L-SOFC509-04 | SOFC509 | 0.6/1kV FR-CV 1C-185㎟-P
X | 365 | L-SOFC509-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 102 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC509 | 05 | L-SOFC509-05 | SOFC509 | 0.6/1kV FR-CV 1C-185㎟-P
X | 366 | L-SOFC509-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 102 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-502 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | K-TF-458 K-TF-124 K-TF-122 | ROUTING PATH 1: K-TF-458; ROUTING PATH 2: K-TF-124; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC509 | 06 | L-SOFC509-06 | SOFC509 | 0.6/1kV FR-CV 1C-185㎟-P
X | 367 | L-WDM501-01 | P | 0.6/1kV | FR-CV | 2C | 16 | 116 | 18.5 | 268.81 | K-PB-672 | 28 | 0.12 | 1.2 | F | 전기실 | EL-LV-503 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #501 | WATER DISTRIBUTION MODULE #501 | K-TF-223 K-TF-216 K-TF-212 | ROUTING PATH 1: K-TF-223; ROUTING PATH 2: K-TF-216; ROUTING PATH 3: K-TF-212 |  |  | L | WDM501 | 01 | L-WDM501-01 | WDM501 | 0.6/1kV FR-CV 2C-16㎟-P
X | 368 | L-WDM502-02 | P | 0.6/1kV | FR-CV | 2C | 16 | 114 | 18.5 | 268.81 | K-PB-673 | 27 | 0.12 | 1.2 | F | 전기실 | EL-LV-503 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #502 | WATER DISTRIBUTION MODULE #502 | K-TF-223 K-TF-216 K-TF-212 | ROUTING PATH 1: K-TF-223; ROUTING PATH 2: K-TF-216; ROUTING PATH 3: K-TF-212 |  |  | L | WDM502 | 02 | L-WDM502-02 | WDM502 | 0.6/1kV FR-CV 2C-16㎟-P
X | 369 | L-TC501-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 118 | 22 | 380.14 | K-PB-661 | 25 | 0.12 | 2.04 | F | 전기실 | EL-LV-503 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | TC #501 | TELE CABINET #501 | K-TF-223 K-TF-216 K-TF-212 | ROUTING PATH 1: K-TF-223; ROUTING PATH 2: K-TF-216; ROUTING PATH 3: K-TF-212 |  |  | L | TC501 | 01 | L-TC501-01 | TC501 | 0.6/1kV FR-CV 2C-25㎟-P
O | 370 | L-EHT501-01 | P | 0.6/1kV | FR-CV | 2C | 6 | 107 | 14 | 153.94 | K-PB-034 | 63 | 0.12 | 0.375 | F | 전기실 | EL-LV-503 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #501 | FUEL CELL EHT #501 | K-TF-123 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-123; ROUTING PATH 2: K-TF-116; ROUTING PATH 3: K-TF-112 |  |  | L | EHT501 | 01 | L-EHT501-01 | EHT501 | 0.6/1kV FR-CV 2C-6㎟-P
X | 371 | L-EHT502-02 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-035 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #501 | FUEL CELL EHT #502 | FUEL CELL AREA | EHT #502 | FUEL CELL EHT #502 | - | [21 empty] | L | EHT502 | 02 | L-EHT502-02 | EHT502 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 372 | L-EHT503-03 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-036 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #502 | FUEL CELL EHT #502 | FUEL CELL AREA | EHT #503 | FUEL CELL EHT #503 | - | [21 empty] | L | EHT503 | 03 | L-EHT503-03 | EHT503 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
O | 373 | L-EHT504-04 | P | 0.6/1kV | FR-CV | 2C | 6 | 96 | 14 | 153.94 | K-PB-163 | 63 | 0.12 | 0.375 | F | 전기실 | EL-LV-503 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #504 | FUEL CELL EHT #504 | K-TF-123 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-123; ROUTING PATH 2: K-TF-116; ROUTING PATH 3: K-TF-112 |  |  | L | EHT504 | 04 | L-EHT504-04 | EHT504 | 0.6/1kV FR-CV 2C-6㎟-P
X | 374 | L-EHT505-05 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-165 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #504 | FUEL CELL EHT #504 | FUEL CELL AREA | EHT #505 | FUEL CELL EHT #505 | - | [21 empty] | L | EHT505 | 05 | L-EHT505-05 | EHT505 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 375 | L-EHT506-06 | P | 0.6/1kV | FR-CV | 2C | 6 | 11 | 14 | 153.94 | K-PA-166 | 11 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #505 | FUEL CELL EHT #505 | FUEL CELL AREA | EHT #506 | FUEL CELL EHT #506 | - | [21 empty] | L | EHT506 | 06 | L-EHT506-06 | EHT506 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 376 | L-EHT507-07 | P | 0.6/1kV | FR-CV | 2C | 6 | 94 | 14 | 153.94 | K-PB-312 | 63 | 0.12 | 0.375 | F | 전기실 | EL-LV-503 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #507 | FUEL CELL EHT #507 | K-TF-123 K-TF-135 K-TF-134 | ROUTING PATH 1: K-TF-123; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-134 |  |  | L | EHT507 | 07 | L-EHT507-07 | EHT507 | 0.6/1kV FR-CV 2C-6㎟-P
X | 377 | L-EHT508-08 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-315 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #507 | FUEL CELL EHT #507 | FUEL CELL AREA | EHT #508 | FUEL CELL EHT #508 | - | [21 empty] | L | EHT508 | 08 | L-EHT508-08 | EHT508 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | 378 | L-EHT509-09 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-316 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #508 | FUEL CELL EHT #508 | FUEL CELL AREA | EHT #509 | FUEL CELL EHT #509 | - | [21 empty] | L | EHT509 | 09 | L-EHT509-09 | EHT509 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X
X | #REF! | L-SOFC602-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 107 | 24 | 452.39 | K-PC-081 | 71 | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | K-TF-462 K-TF-236 K-TF-224 K-TF-217 K-TF-208 K-TF-202 | ROUTING PATH 1: K-TF-462; ROUTING PATH 2: K-TF-236; ROUTING PATH 3: K-TF-224; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-208; ROUTING PATH 6: K-TF-202 |  |  | L | SOFC602 | 01 | L-SOFC602-01 | SOFC602 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC602-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 107 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | K-TF-462 K-TF-236 K-TF-224 K-TF-217 K-TF-208 K-TF-202 | ROUTING PATH 1: K-TF-462; ROUTING PATH 2: K-TF-236; ROUTING PATH 3: K-TF-224; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-208; ROUTING PATH 6: K-TF-202 |  |  | L | SOFC602 | 02 | L-SOFC602-02 | SOFC602 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC602-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 107 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | K-TF-462 K-TF-236 K-TF-224 K-TF-217 K-TF-208 K-TF-202 | ROUTING PATH 1: K-TF-462; ROUTING PATH 2: K-TF-236; ROUTING PATH 3: K-TF-224; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-208; ROUTING PATH 6: K-TF-202 |  |  | L | SOFC602 | 03 | L-SOFC602-03 | SOFC602 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC602-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 107 | 24 | 452.39 | K-PC-082 | 71 | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | K-TF-462 K-TF-236 K-TF-224 K-TF-217 K-TF-208 K-TF-202 | ROUTING PATH 1: K-TF-462; ROUTING PATH 2: K-TF-236; ROUTING PATH 3: K-TF-224; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-208; ROUTING PATH 6: K-TF-202 |  |  | L | SOFC602 | 04 | L-SOFC602-04 | SOFC602 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC602-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 107 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | K-TF-462 K-TF-236 K-TF-224 K-TF-217 K-TF-208 K-TF-202 | ROUTING PATH 1: K-TF-462; ROUTING PATH 2: K-TF-236; ROUTING PATH 3: K-TF-224; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-208; ROUTING PATH 6: K-TF-202 |  |  | L | SOFC602 | 05 | L-SOFC602-05 | SOFC602 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC602-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 107 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | K-TF-462 K-TF-236 K-TF-224 K-TF-217 K-TF-208 K-TF-202 | ROUTING PATH 1: K-TF-462; ROUTING PATH 2: K-TF-236; ROUTING PATH 3: K-TF-224; ROUTING PATH 4: K-TF-217; ROUTING PATH 5: K-TF-208; ROUTING PATH 6: K-TF-202 |  |  | L | SOFC602 | 06 | L-SOFC602-06 | SOFC602 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC605-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-233 | 71 | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC605 | 01 | L-SOFC605-01 | SOFC605 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC605-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC605 | 02 | L-SOFC605-02 | SOFC605 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC605-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC605 | 03 | L-SOFC605-03 | SOFC605 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC605-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-234 | 71 | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC605 | 04 | L-SOFC605-04 | SOFC605 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC605-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC605 | 05 | L-SOFC605-05 | SOFC605 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC605-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC605 | 06 | L-SOFC605-06 | SOFC605 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC606-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-271 | 71 | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC606 | 01 | L-SOFC606-01 | SOFC606 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC606-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC606 | 02 | L-SOFC606-02 | SOFC606 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC606-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC606 | 03 | L-SOFC606-03 | SOFC606 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC606-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 | K-PC-272 | 71 | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC606 | 04 | L-SOFC606-04 | SOFC606 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC606-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC606 | 05 | L-SOFC606-05 | SOFC606 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC606-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 96 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-602 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | K-TF-461 K-TF-135 K-TF-122 | ROUTING PATH 1: K-TF-461; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-122 |  |  | L | SOFC606 | 06 | L-SOFC606-06 | SOFC606 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-WDM601-01 | P | 0.6/1kV | FR-CV | 2C | 16 | 115 | 18.5 | 268.81 | K-PB-681 | 40 | 0.12 | 1.2 | F | 전기실 | EL-LV-603 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #601 | WATER DISTRIBUTION MODULE #601 | K-TF-235 K-TF-223 K-TF-216 K-TF-212 | ROUTING PATH 1: K-TF-235; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-216; ROUTING PATH 4: K-TF-212 |  |  | L | WDM601 | 01 | L-WDM601-01 | WDM601 | 0.6/1kV FR-CV 2C-16㎟-P
X | #REF! | L-WDM602-02 | P | 0.6/1kV | FR-CV | 2C | 16 | 117 | 18.5 | 268.81 | K-PB-682 | 39 | 0.12 | 1.2 | F | 전기실 | EL-LV-603 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #602 | WATER DISTRIBUTION MODULE #602 | K-TF-235 K-TF-223 K-TF-216 K-TF-212 | ROUTING PATH 1: K-TF-235; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-216; ROUTING PATH 4: K-TF-212 |  |  | L | WDM602 | 02 | L-WDM602-02 | WDM602 | 0.6/1kV FR-CV 2C-16㎟-P
X | #REF! | L-TC601-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 113 | 22 | 380.14 | K-PB-671 | 33 | 0.12 | 2.04 | F | 전기실 | EL-LV-603 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | TC #601 | TELE CABINET #601 | K-TF-235 K-TF-223 K-TF-216 K-TF-212 | ROUTING PATH 1: K-TF-235; ROUTING PATH 2: K-TF-223; ROUTING PATH 3: K-TF-216; ROUTING PATH 4: K-TF-212 |  |  | L | TC601 | 01 | L-TC601-01 | TC601 | 0.6/1kV FR-CV 2C-25㎟-P
O | #REF! | L-EHT601-01 | P | 0.6/1kV | FR-CV | 2C | 6 | 105 | 14 | 153.94 | K-PB-031 | 71 | 0.12 | 0.375 | F | 전기실 | EL-LV-603 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #601 | FUEL CELL EHT #601 | K-TF-135 K-TF-123 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-135; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-116; ROUTING PATH 4: K-TF-112 |  |  | L | EHT601 | 01 | L-EHT601-01 | EHT601 | 0.6/1kV FR-CV 2C-6㎟-P
X | #REF! | L-EHT602-02 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-037 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #602 | FUEL CELL EHT #601 | FUEL CELL AREA | EHT #602 | FUEL CELL EHT #602 | - | [21 empty] | L | EHT602 | 02 | L-EHT602-02 | EHT602 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT603-03 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-038 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #602 | FUEL CELL EHT #602 | FUEL CELL AREA | EHT #603 | FUEL CELL EHT #603 | - | [21 empty] | L | EHT603 | 03 | L-EHT603-03 | EHT603 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
O | #REF! | L-EHT604-04 | P | 0.6/1kV | FR-CV | 2C | 6 | 98 | 14 | 153.94 | K-PB-164 | 71 | 0.12 | 0.375 | F | 전기실 | EL-LV-603 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #604 | FUEL CELL EHT #604 | K-TF-135 K-TF-123 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-135; ROUTING PATH 2: K-TF-123; ROUTING PATH 3: K-TF-116; ROUTING PATH 4: K-TF-112 |  |  | L | EHT604 | 04 | L-EHT604-04 | EHT604 | 0.6/1kV FR-CV 2C-6㎟-P
X | #REF! | L-EHT605-05 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-167 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #604 | FUEL CELL EHT #604 | FUEL CELL AREA | EHT #605 | FUEL CELL EHT #605 | - | [21 empty] | L | EHT605 | 05 | L-EHT605-05 | EHT605 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT606-06 | P | 0.6/1kV | FR-CV | 2C | 6 | 11 | 14 | 153.94 | K-PA-168 | 11 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #605 | FUEL CELL EHT #605 | FUEL CELL AREA | EHT #606 | FUEL CELL EHT #606 | - | [21 empty] | L | EHT606 | 06 | L-EHT606-06 | EHT606 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT607-07 | P | 0.6/1kV | FR-CV | 2C | 6 | 92 | 14 | 153.94 | K-PB-311 | 71 | 0.12 | 0.375 | F | 전기실 | EL-LV-603 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #607 | FUEL CELL EHT #607 | K-TF-235 K-TF-234 | ROUTING PATH 1: K-TF-235; ROUTING PATH 2: K-TF-234 |  |  | L | EHT607 | 07 | L-EHT607-07 | EHT607 | 0.6/1kV FR-CV 2C-6㎟-P
X | #REF! | L-EHT608-08 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-317 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #607 | FUEL CELL EHT #607 | FUEL CELL AREA | EHT #608 | FUEL CELL EHT #608 | - | [21 empty] | L | EHT608 | 08 | L-EHT608-08 | EHT608 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT609-09 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-318 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #608 | FUEL CELL EHT #608 | FUEL CELL AREA | EHT #609 | FUEL CELL EHT #609 | - | [21 empty] | L | EHT609 | 09 | L-EHT609-09 | EHT609 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X
X | #REF! | L-SOFC701-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 136 | 24 | 452.39 | K-PC-042 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC701 | 01 | L-SOFC701-01 | SOFC701 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC701-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 136 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC701 | 02 | L-SOFC701-02 | SOFC701 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC701-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 136 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC701 | 03 | L-SOFC701-03 | SOFC701 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC701-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 136 | 24 | 452.39 | K-PC-043 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC701 | 04 | L-SOFC701-04 | SOFC701 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC701-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 136 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC701 | 05 | L-SOFC701-05 | SOFC701 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC701-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 136 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC701 | 06 | L-SOFC701-06 | SOFC701 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC702-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 133 | 24 | 452.39 | K-PC-083 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC702 | 01 | L-SOFC702-01 | SOFC702 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC702-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 133 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC702 | 02 | L-SOFC702-02 | SOFC702 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC702-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 133 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC702 | 03 | L-SOFC702-03 | SOFC702 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC702-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 133 | 24 | 452.39 | K-PC-084 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC702 | 04 | L-SOFC702-04 | SOFC702 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC702-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 133 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC702 | 05 | L-SOFC702-05 | SOFC702 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC702-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 133 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC702 | 06 | L-SOFC702-06 | SOFC702 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC703-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 | K-PC-121 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC703 | 01 | L-SOFC703-01 | SOFC703 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC703-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC703 | 02 | L-SOFC703-02 | SOFC703 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC703-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC703 | 03 | L-SOFC703-03 | SOFC703 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC703-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 | K-PC-122 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC703 | 04 | L-SOFC703-04 | SOFC703 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC703-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC703 | 05 | L-SOFC703-05 | SOFC703 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC703-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC703 | 06 | L-SOFC703-06 | SOFC703 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC704-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 | K-PC-173 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC704 | 01 | L-SOFC704-01 | SOFC704 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC704-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC704 | 02 | L-SOFC704-02 | SOFC704 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC704-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC704 | 03 | L-SOFC704-03 | SOFC704 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC704-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 | K-PC-174 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC704 | 04 | L-SOFC704-04 | SOFC704 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC704-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC704 | 05 | L-SOFC704-05 | SOFC704 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC704-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 128 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | K-TF-466 K-TF-144 K-TF-139 | ROUTING PATH 1: K-TF-466; ROUTING PATH 2: K-TF-144; ROUTING PATH 3: K-TF-139 |  |  | L | SOFC704 | 06 | L-SOFC704-06 | SOFC704 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC705-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 | K-PC-231 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC705 | 01 | L-SOFC705-01 | SOFC705 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC705-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC705 | 02 | L-SOFC705-02 | SOFC705 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC705-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC705 | 03 | L-SOFC705-03 | SOFC705 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC705-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 | K-PC-232 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC705 | 04 | L-SOFC705-04 | SOFC705 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC705-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC705 | 05 | L-SOFC705-05 | SOFC705 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC705-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC705 | 06 | L-SOFC705-06 | SOFC705 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC706-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 | K-PC-273 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC706 | 01 | L-SOFC706-01 | SOFC706 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC706-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC706 | 02 | L-SOFC706-02 | SOFC706 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC706-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC706 | 03 | L-SOFC706-03 | SOFC706 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC706-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 | K-PC-274 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC706 | 04 | L-SOFC706-04 | SOFC706 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC706-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC706 | 05 | L-SOFC706-05 | SOFC706 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC706-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | K-TF-465 K-TF-243 K-TF-239 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-239 |  |  | L | SOFC706 | 06 | L-SOFC706-06 | SOFC706 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC707-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 | K-PC-322 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC707 | 01 | L-SOFC707-01 | SOFC707 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC707-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC707 | 02 | L-SOFC707-02 | SOFC707 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC707-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC707 | 03 | L-SOFC707-03 | SOFC707 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC707-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 | K-PC-323 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC707 | 04 | L-SOFC707-04 | SOFC707 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC707-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC707 | 05 | L-SOFC707-05 | SOFC707 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC707-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC707 | 06 | L-SOFC707-06 | SOFC707 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC708-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 | K-PC-363 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC708 | 01 | L-SOFC708-01 | SOFC708 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC708-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC708 | 02 | L-SOFC708-02 | SOFC708 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC708-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC708 | 03 | L-SOFC708-03 | SOFC708 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC708-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 | K-PC-364 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC708 | 04 | L-SOFC708-04 | SOFC708 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC708-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC708 | 05 | L-SOFC708-05 | SOFC708 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC708-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 119 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC708 | 06 | L-SOFC708-06 | SOFC708 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC709-01 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 | K-PC-741 | 85 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC709 | 01 | L-SOFC709-01 | SOFC709 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC709-02 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC709 | 02 | L-SOFC709-02 | SOFC709 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC709-03 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC709 | 03 | L-SOFC709-03 | SOFC709 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC709-04 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 | K-PC-742 | 91 | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC709 | 04 | L-SOFC709-04 | SOFC709 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC709-05 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC709 | 05 | L-SOFC709-05 | SOFC709 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-SOFC709-06 | P | 0.6/1kV | FR-CV | 1C | 185 | 123 | 24 | 452.39 |  |  | 0.48 | 300 | F | 전기실 | EL-LV-702 | 480V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | K-TF-465 K-TF-243 K-TF-249 | ROUTING PATH 1: K-TF-465; ROUTING PATH 2: K-TF-243; ROUTING PATH 3: K-TF-249 |  |  | L | SOFC709 | 06 | L-SOFC709-06 | SOFC709 | 0.6/1kV FR-CV 1C-185㎟-P
X | #REF! | L-WDM701-01 | P | 0.6/1kV | FR-CV | 2C | 16 | 140 | 18.5 | 268.81 | K-PB-691 | 57 | 0.12 | 1.2 | F | 전기실 | EL-LV-703 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #701 | WATER DISTRIBUTION MODULE #701 | K-TF-143 K-TF-136 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-143; ROUTING PATH 2: K-TF-136; ROUTING PATH 3: K-TF-124; ROUTING PATH 4: K-TF-117; ROUTING PATH 5: K-TF-108; ROUTING PATH 6: K-TF-102 |  |  | L | WDM701 | 01 | L-WDM701-01 | WDM701 | 0.6/1kV FR-CV 2C-16㎟-P
X | #REF! | L-WDM702-02 | P | 0.6/1kV | FR-CV | 2C | 16 | 142 | 18.5 | 268.81 | K-PB-692 | 56 | 0.12 | 1.2 | F | 전기실 | EL-LV-703 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | WDM #702 | WATER DISTRIBUTION MODULE #702 | K-TF-143 K-TF-136 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-143; ROUTING PATH 2: K-TF-136; ROUTING PATH 3: K-TF-124; ROUTING PATH 4: K-TF-117; ROUTING PATH 5: K-TF-108; ROUTING PATH 6: K-TF-102 |  |  | L | WDM702 | 02 | L-WDM702-02 | WDM702 | 0.6/1kV FR-CV 2C-16㎟-P
X | #REF! | L-TC701-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 138 | 22 | 380.14 | K-PB-693 | 49 | 0.12 | 2.04 | F | 전기실 | EL-LV-703 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | TC #701 | TELE CABINET #701 | K-TF-143 K-TF-136 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-143; ROUTING PATH 2: K-TF-136; ROUTING PATH 3: K-TF-124; ROUTING PATH 4: K-TF-117; ROUTING PATH 5: K-TF-108; ROUTING PATH 6: K-TF-102 |  |  | L | TC701 | 01 | L-TC701-01 | TC701 | 0.6/1kV FR-CV 2C-25㎟-P
X | #REF! | L-EHT701-01 | P | 0.6/1kV | FR-CV | 2C | 6 | 130 | 14 | 153.94 | K-PB-041 | 85 | 0.12 | 0.375 | F | 전기실 | EL-LV-703 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #701 | FUEL CELL EHT #701 | K-TF-143 K-TF-136 K-TF-124 K-TF-117 K-TF-108 K-TF-102 | ROUTING PATH 1: K-TF-143; ROUTING PATH 2: K-TF-136; ROUTING PATH 3: K-TF-124; ROUTING PATH 4: K-TF-117; ROUTING PATH 5: K-TF-108; ROUTING PATH 6: K-TF-102 |  |  | L | EHT701 | 01 | L-EHT701-01 | EHT701 | 0.6/1kV FR-CV 2C-6㎟-P
X | #REF! | L-EHT702-02 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-044 | 10 | 0.12 | 0.375 | F | 전기실 | EHT #702 | FUEL CELL EHT #701 | FUEL CELL AREA | EHT #702 | FUEL CELL EHT #702 | - | [21 empty] | L | EHT702 | 02 | L-EHT702-02 | EHT702 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT703-03 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-045 | 8 | 0.12 | 0.375 | F | 전기실 | EHT #702 | FUEL CELL EHT #702 | FUEL CELL AREA | EHT #703 | FUEL CELL EHT #703 | - | [21 empty] | L | EHT703 | 03 | L-EHT703-03 | EHT703 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
O | #REF! | L-EHT704-04 | P | 0.6/1kV | FR-CV | 2C | 6 | 123 | 14 | 153.94 | K-PB-175 | 85 | 0.12 | 0.375 | F | 전기실 | EL-LV-703 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #704 | FUEL CELL EHT #704 | K-TF-143 K-TF-135 K-TF-123 K-TF-116 K-TF-112 | ROUTING PATH 1: K-TF-143; ROUTING PATH 2: K-TF-135; ROUTING PATH 3: K-TF-123; ROUTING PATH 4: K-TF-116; ROUTING PATH 5: K-TF-112 |  |  | L | EHT704 | 04 | L-EHT704-04 | EHT704 | 0.6/1kV FR-CV 2C-6㎟-P
X | #REF! | L-EHT705-05 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-176 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #704 | FUEL CELL EHT #704 | FUEL CELL AREA | EHT #705 | FUEL CELL EHT #705 | - | [21 empty] | L | EHT705 | 05 | L-EHT705-05 | EHT705 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT706-06 | P | 0.6/1kV | FR-CV | 2C | 6 | 11 | 14 | 153.94 | K-PA-177 | 11 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #705 | FUEL CELL EHT #705 | FUEL CELL AREA | EHT #706 | FUEL CELL EHT #706 | - | [21 empty] | L | EHT706 | 06 | L-EHT706-06 | EHT706 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT707-07 | P | 0.6/1kV | FR-CV | 2C | 6 | 117 | 14 | 153.94 | K-PB-321 | 85 | 0.12 | 0.375 | F | 전기실 | EL-LV-703 | 120V DISTRIBUTION BOARD(F/C) | FUEL CELL AREA | EHT #707 | FUEL CELL EHT #707 | K-TF-143 K-TF-149 | ROUTING PATH 1: K-TF-143; ROUTING PATH 2: K-TF-149 |  |  | L | EHT707 | 07 | L-EHT707-07 | EHT707 | 0.6/1kV FR-CV 2C-6㎟-P
X | #REF! | L-EHT708-08 | P | 0.6/1kV | FR-CV | 2C | 6 | 10 | 14 | 153.94 | K-PA-326 | 10 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #707 | FUEL CELL EHT #707 | FUEL CELL AREA | EHT #708 | FUEL CELL EHT #708 | - | [21 empty] | L | EHT708 | 08 | L-EHT708-08 | EHT708 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X | #REF! | L-EHT709-09 | P | 0.6/1kV | FR-CV | 2C | 6 | 8 | 14 | 153.94 | K-PA-327 | 8 | 0.12 | 0.375 | F | FUEL CELL AREA | EHT #708 | FUEL CELL EHT #708 | FUEL CELL AREA | EHT #709 | FUEL CELL EHT #709 | - | [21 empty] | L | EHT709 | 09 | L-EHT709-09 | EHT709 | 0.6/1kV FR-CV 2C-6㎟-P | bar: ROUTING PATH 1
X
X | #REF! | L-ELAVR001-01 | P | 0.6/1kV | FR-CV | 2C | 25 | 30 | 22 | 380.14 | - | - | 0.38 | 20 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-AVR-001 | AVR PANEL | K-TF-329 K-TF-328 K-TF-338 K-TF-342 K-TB-354 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-338; ROUTING PATH 4: K-TF-342; ROUTING PATH 5: K-TB-354 |  |  | L | ELAVR001 | 01 | L-ELAVR001-01 | ELAVR001 | 0.6/1kV FR-CV 2C-25㎟-P
X | #REF! | L-ELHF001-01 | P | 0.6/1kV | FR-CV | 4C | 25 | 70 | 26 | 530.93 | K-PC-181 | 4 | 0.38 | 31.5 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | FUEL CELL AREA | EL-HF-001 | EHT PNL | K-TF-329 K-TF-328 K-TF-333 K-TF-332 K-TF-322 K-PC-564 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-333; ROUTING PATH 4: K-TF-332; ROUTING PATH 5: K-TF-322; ROUTING PATH 6: K-PC-564 |  |  | L | ELHF001 | 01 | L-ELHF001-01 | ELHF001 | 0.6/1kV FR-CV 4C-25㎟-P
X | #REF! | L-HVPC001A-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 44 | 20 | 314.16 | K-RC-801 | 16 | 0.38 | 21 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001A | PACKAGED AIR CONDITIONER-A | K-TF-329 K-TF-328 K-TF-338 K-TF-341 K-TF-340 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-338; ROUTING PATH 4: K-TF-341; ROUTING PATH 5: K-TF-340 |  |  | L | HVPC001A | 01 | L-HVPC001A-01 | HVPC001A | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001B-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 46 | 20 | 314.16 | K-RC-802 | 18 | 0.38 | 21 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001B | PACKAGED AIR CONDITIONER-B | K-TF-329 K-TF-328 K-TF-338 K-TF-341 K-TF-340 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-338; ROUTING PATH 4: K-TF-341; ROUTING PATH 5: K-TF-340 |  |  | L | HVPC001B | 01 | L-HVPC001B-01 | HVPC001B | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001C-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 48 | 20 | 314.16 | K-RC-803 | 20 | 0.38 | 21 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001C | PACKAGED AIR CONDITIONER-C | K-TF-329 K-TF-328 K-TF-338 K-TF-341 K-TF-340 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-338; ROUTING PATH 4: K-TF-341; ROUTING PATH 5: K-TF-340 |  |  | L | HVPC001C | 01 | L-HVPC001C-01 | HVPC001C | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001D-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 50 | 20 | 314.16 | K-RC-804 | 22 | 0.38 | 21 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001D | PACKAGED AIR CONDITIONER-D | K-TF-329 K-TF-328 K-TF-338 K-TF-341 K-TF-340 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-338; ROUTING PATH 4: K-TF-341; ROUTING PATH 5: K-TF-340 |  |  | L | HVPC001D | 01 | L-HVPC001D-01 | HVPC001D | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001E-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 52 | 20 | 314.16 | K-RC-805 | 24 | 0.38 | 21 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001E | PACKAGED AIR CONDITIONER-E | K-TF-329 K-TF-328 K-TF-338 K-TF-341 K-TF-340 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-338; ROUTING PATH 4: K-TF-341; ROUTING PATH 5: K-TF-340 |  |  | L | HVPC001E | 01 | L-HVPC001E-01 | HVPC001E | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001F-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 42 | 20 | 314.16 | K-RC-806 | 18 | 0.38 | 21 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001F | PACKAGED AIR CONDITIONER-F | K-TF-330 K-TF-338 K-TF-341 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-341 |  |  | L | HVPC001F | 01 | L-HVPC001F-01 | HVPC001F | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-MEPP001A-01 | P | 0.6/1kV | FR-CV | 4C | 6 | 35 | 16 | 201.07 | K-PB-807 | 7 | 0.22 | 2.5 | F | 전기실 | LATER | APM PANEL | 전기실 북쪽 | ME-PP-001A | CITY WATER PUMP LCP | K-TF-329 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-318; ROUTING PATH 3: K-TB-315 |  | 191015 | L | MEPP001A | 01 | L-MEPP001A-01 | MEPP001A | 0.6/1kV FR-CV 4C-6㎟-P
X | #REF! | L-ELHV001-01 | P | 0.6/1kV | FR-CV | 2C | 16 | 32 | 18.5 | 268.81 | - | - | 0.22 | 6 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-HV-001 | 22.9kV SWITCHGEAR (INCOMING VCB) | K-TF-329 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-318; ROUTING PATH 3: K-TB-315 |  |  | L | ELHV001 | 01 | L-ELHV001-01 | ELHV001 | 0.6/1kV FR-CV 2C-16㎟-P
X | #REF! | L-ELLV101-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 35 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-101 | 480V SWITCHGEAR (ACB) | K-TF-329 K-TF-318 K-TF-314 K-TF-313 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-318; ROUTING PATH 3: K-TF-314; ROUTING PATH 4: K-TF-313 |  |  | L | ELLV101 | 01 | L-ELLV101-01 | ELLV101 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV201-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 33 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-201 | 480V SWITCHGEAR (ACB) | K-TF-329 K-TF-321 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-321 |  |  | L | ELLV201 | 01 | L-ELLV201-01 | ELLV201 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV301-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 20 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-301 | 480V SWITCHGEAR (ACB) | K-TF-329 K-TF-328 K-TF-333 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-333 |  |  | L | ELLV301 | 01 | L-ELLV301-01 | ELLV301 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV401-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 35 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-401 | 480V SWITCHGEAR (ACB) | K-TF-329 K-TF-328 K-TF-338 K-TF-341 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-338; ROUTING PATH 4: K-TF-341 |  |  | L | ELLV401 | 01 | L-ELLV401-01 | ELLV401 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-LATER-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 48 | 13 | 132.74 | K-PA-808 | 10 | 0.22 | 0.3 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 북쪽 | LATER | NG GOVERNOR LTG | K-TF-329 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-318; ROUTING PATH 3: K-TB-315 |  |  | L | LATER | 01 | L-LATER-01 | LATER | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-LATER-02 | P | 0.6/1kV | FR-CV | 4C | 6 | 25 | 16 | 201.07 | - | 10 | 0.22 | 2.5 | F | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전기실 북쪽 | LATER | APM PANEL | [22 empty] | L | LATER | 02 | L-LATER-02 | LATER | 0.6/1kV FR-CV 4C-6㎟-P
X | #REF! | L-LATER-03 | P | 0.6/1kV | FR-CV | 2C | 35 | 80 | 24 | 452.39 | - | 10 | DC 390 | 2.5 | F | 전기실 | SOFC #201 | FUEL CELL #401 | 전기실 북쪽 | LATER | APM PANEL | [22 empty] | L | LATER | 03 | L-LATER-03 | LATER | 0.6/1kV FR-CV 2C-35㎟-P
X | #REF! | L-LATER-04 | P | 0.6/1kV | FR-CV | 2C | 35 | 105 | 24 | 452.39 | - | 10 | DC 390 | 2.5 | F | 전기실 | SOFC #401 | FUEL CELL #401 | 전기실 북쪽 | LATER | APM PANEL | [22 empty] | L | LATER | 04 | L-LATER-04 | LATER | 0.6/1kV FR-CV 2C-35㎟-P
X
X | #REF! | L-ELUPS&DC001-01 | P | 0.6/1kV | FR-CV | 3C | 25 | 32 | 23 | 415.48 | - | - | 0.38 | 30 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-UPS&DC-001 | B/C | K-TF-330 K-TF-338 K-TF-342 K-TB-354 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-342; ROUTING PATH 4: K-TB-354 |  |  | L | ELUPS&DC001 | 01 | L-ELUPS&DC001-01 | ELUPS&DC001 | 0.6/1kV FR-CV 3C-25㎟-P
X | #REF! | L-ELHF002-02 | P | 0.6/1kV | FR-CV | 4C | 25 | 95 | 26 | 530.93 | K-PC-371 | 4 | 0.38 | 31.5 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | FUEL CELL AREA | EL-HF-002 | EHT PNL | K-TF-329 K-TF-328 K-TF-333 K-TF-332 K-TF-322 K-PC-564 | ROUTING PATH 1: K-TF-329; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-333; ROUTING PATH 4: K-TF-332; ROUTING PATH 5: K-TF-322; ROUTING PATH 6: K-PC-564 |  |  | L | ELHF002 | 02 | L-ELHF002-02 | ELHF002 | 0.6/1kV FR-CV 4C-25㎟-P
X | #REF! | L-ELLP001-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 20 | 20 | 314.16 | K-RC-809 | 10 | 0.38 | 25 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LP-001 | LIGHTING PNL | K-TF-330 | ROUTING PATH 1: K-TF-330 |  |  | L | ELLP001 | 01 | L-ELLP001-01 | ELLP001 | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001G-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 34 | 20 | 314.16 | K-RC-810 | 16 | 0.38 | 21 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001G | PACKAGED AIR CONDITIONER-G | K-TF-330 K-TF-338 K-TF-341 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-341 |  |  | L | HVPC001G | 01 | L-HVPC001G-01 | HVPC001G | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001H-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 28 | 20 | 314.16 | K-RC-811 | 21 | 0.38 | 21 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001H | PACKAGED AIR CONDITIONER-H | K-TF-330 | ROUTING PATH 1: K-TF-330 |  |  | L | HVPC001H | 01 | L-HVPC001H-01 | HVPC001H | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001I-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 26 | 20 | 314.16 | K-RC-812 | 19 | 0.38 | 21 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001I | PACKAGED AIR CONDITIONER-I | K-TF-330 | ROUTING PATH 1: K-TF-330 |  |  | L | HVPC001I | 01 | L-HVPC001I-01 | HVPC001I | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001J-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 24 | 20 | 314.16 | K-RC-813 | 17 | 0.38 | 21 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001J | PACKAGED AIR CONDITIONER-J | K-TF-330 | ROUTING PATH 1: K-TF-330 |  |  | L | HVPC001J | 01 | L-HVPC001J-01 | HVPC001J | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001K-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 48 | 20 | 314.16 | K-RC-814 | 17 | 0.38 | 21 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001K | PACKAGED AIR CONDITIONER-K | K-TF-330 K-TF-328 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-318; ROUTING PATH 4: K-TB-315 |  |  | L | HVPC001K | 01 | L-HVPC001K-01 | HVPC001K | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-HVPC001L-01 | P | 0.6/1kV | FR-CV | 4C | 10 | 46 | 20 | 314.16 | K-RC-815 | 15 | 0.38 | 21 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | HV-PC-001L | PACKAGED AIR CONDITIONER-L | K-TF-330 K-TF-328 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-318; ROUTING PATH 4: K-TB-315 |  |  | L | HVPC001L | 01 | L-HVPC001L-01 | HVPC001L | 0.6/1kV FR-CV 4C-10㎟-P
X | #REF! | L-ELEP001A-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 30 | 13 | 132.74 | K-PA-816 | 23 | 0.22 | 2.8 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | FUEL CELL AREA | EL-EP-001A | OUTDOOR UNIT OF E.H.P | K-TF-330 | ROUTING PATH 1: K-TF-330 |  |  | L | ELEP001A | 01 | L-ELEP001A-01 | ELEP001A | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-MEPP001B-01 | P | 0.6/1kV | FR-CV | 3C | 6 | 35 | 14.5 | 165.13 | K-PB-817 | 7 | 0.22 | 2.5 | M | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 북쪽 | ME-PP-001B | CITY WATER PUMP LCP | K-TF-330 K-TF-328 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-318; ROUTING PATH 4: K-TB-315 |  |  | L | MEPP001B | 01 | L-MEPP001B-01 | MEPP001B | 0.6/1kV FR-CV 3C-6㎟-P
X | #REF! | L-ELLV501-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 26 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-501 | 480V SWITCHGEAR (ACB) | K-TF-330 K-TF-328 K-TF-321 K-TF-320 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-321; ROUTING PATH 4: K-TF-320 |  |  | L | ELLV501 | 01 | L-ELLV501-01 | ELLV501 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV601-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 38 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-601 | 480V SWITCHGEAR (ACB) | K-TF-330 K-TF-333 K-TF-332 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-333; ROUTING PATH 3: K-TF-332 |  |  | L | ELLV601 | 01 | L-ELLV601-01 | ELLV601 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV701-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 30 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-701 | 480V SWITCHGEAR (ACB) | K-TF-330 K-TF-338 K-TF-341 K-TF-340 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-341; ROUTING PATH 4: K-TF-340 |  |  | L | ELLV701 | 01 | L-ELLV701-01 | ELLV701 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV801-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 10 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-801 | 380/220V SWITCHGEAR (ACB) | K-TF-330 K-TF-328 K-TF-329 | ROUTING PATH 1: K-TF-330; ROUTING PATH 2: K-TF-328; ROUTING PATH 3: K-TF-329 |  |  | L | ELLV801 | 01 | L-ELLV801-01 | ELLV801 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV901-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 10 | 13 | 132.74 | - | - | 0.22 | 0.5 | F | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전기실 | EL-LV-901 | 380/220V SWITCHGEAR (ACB) | - | [21 empty] | L | ELLV901 | 01 | L-ELLV901-01 | ELLV901 | 0.6/1kV FR-CV 2C-4㎟-P | bar: ROUTING PATH 1
X
X | #REF! | L-INPLC001-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 28 | 13 | 132.74 | - | - | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전자기기실 | IN-PLC-001 | PLC SYSTEM(MAIN) | K-TB-351 K-TB-352 K-TB-370 | ROUTING PATH 1: K-TB-351; ROUTING PATH 2: K-TB-352; ROUTING PATH 3: K-TB-370 |  | 190822 | L | INPLC001 | 02 | L-INPLC001-02 | INPLC001 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-INPLC001-03 | P | 0.6/1kV | FR-CV | 2C | 4 | 28 | 13 | 132.74 | - | - | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전자기기실 | IN-PLC-001 | PLC SYSTEM(BACK-UP) | K-TB-351 K-TB-352 K-TB-370 | ROUTING PATH 1: K-TB-351; ROUTING PATH 2: K-TB-352; ROUTING PATH 3: K-TB-370 |  | 190822 | L | INPLC001 | 03 | L-INPLC001-03 | INPLC001 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELMDF001-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 27 | 13 | 132.74 | - | - | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전자기기실 | EL-MDF-001 | MDF & CCTV PANEL | K-TB-351 K-TB-352 K-TB-370 | ROUTING PATH 1: K-TB-351; ROUTING PATH 2: K-TB-352; ROUTING PATH 3: K-TB-370 |  | 190822 | L | ELMDF001 | 01 | L-ELMDF001-01 | ELMDF001 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-GDRP-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 26 | 13 | 132.74 | - | - | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전자기기실 | GDRP | GAS DETECTOR PANEL | K-TB-351 K-TB-352 K-TB-370 | ROUTING PATH 1: K-TB-351; ROUTING PATH 2: K-TB-352; ROUTING PATH 3: K-TB-370 |  | 190822 | L | GDRP | 01 | L-GDRP-01 | GDRP | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-INOWS001-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 30 | 13 | 132.74 | K-RB-821 | 8 | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전자기기실 | IN-OWS-001 | OWS | K-TB-351 K-TB-352 K-TB-370 | ROUTING PATH 1: K-TB-351; ROUTING PATH 2: K-TB-352; ROUTING PATH 3: K-TB-370 |  | 190822 | L | INOWS001 | 01 | L-INOWS001-01 | LATER | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-FFFA001-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 31 | 13 | 132.74 | - | - | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전자기기실 | FF-FA-001 | 소방수신반 | K-TB-351 K-TB-352 K-TB-370 | ROUTING PATH 1: K-TB-351; ROUTING PATH 2: K-TB-352; ROUTING PATH 3: K-TB-370 |  | 190822 | L | FFFA001 | 01 | L-FFFA001-01 | LATER | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-SIGNBOARD-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 25 | 13 | 132.74 | K-PA-823 | 6 | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전기실 동쪽 | SIGNBOARD | 옥외현황판 | K-TF-342 K-TF-338 K-TF-328 K-TF-329 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-328; ROUTING PATH 4: K-TF-329 |  | 190822 | L | SIGNBOARD | 01 | L-SIGNBOARD-01 | LATER | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELMDF001-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 27 | 13 | 132.74 | - | - | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전자기기실 | EL-CCTV-001 | CCTV CLIENT PC | K-TB-351 K-TB-352 K-TB-370 | ROUTING PATH 1: K-TB-351; ROUTING PATH 2: K-TB-352; ROUTING PATH 3: K-TB-370 |  | 190822 | L | ELMDF001 | 02 | L-ELMDF001-02 | LATER | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-FC1FQIT101-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 47 | 13 | 132.74 | K-PA-825 | 8 | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전기실 북쪽 | FC1-FQIT-101 | WATER FLOW METER | K-TF-342 K-TF-338 K-TF-328 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-328; ROUTING PATH 4: K-TF-318; ROUTING PATH 5: K-TB-315 |  |  | L | FC1FQIT101 | 01 | L-FC1FQIT101-01 | FC1FQIT101 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-FFFA002-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 25 | 13 | 132.74 | K-RB-826 | 10 | 0.22 |  | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 소화약재실 | FF-FA-002 | 소화약제제어반 | K-TB-351 | ROUTING PATH 1: K-TB-351 |  | 190822 | L | FFFA002 | 01 | L-FFFA002-01 | LATER | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-MEPP001-01 | P | 0.6/1kV | FR-CV | 2C | 4 | 42 | 13 | 132.74 | K-PB-807 | - | 0.22 | 0.05 | F | 전기실 | EL-DP-001 | 220V UPS DISTRIBUTION BOARD | 전기실 북쪽 | ME-PP-001 | CITY WATER PUMP LCP | K-TF-342 K-TF-338 K-TF-328 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-328; ROUTING PATH 4: K-TF-318; ROUTING PATH 5: K-TB-315 |  | 191015 | L | MEPP001 | 01 | L-MEPP001-01 | MEPP001 | 0.6/1kV FR-CV 2C-4㎟-P
X
X | #REF! | L-ELHV001-02 | P | 0.6/1kV | FR-CV | 2C | 16 | 40 | 18.5 | 268.81 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-HV-001 | 22.9kV SWITCHGEAR | K-TF-342 K-TF-338 K-TF-328 K-TF-318 K-TB-315 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-328; ROUTING PATH 4: K-TF-318; ROUTING PATH 5: K-TB-315 |  |  | L | ELHV001 | 02 | L-ELHV001-02 | ELHV001 | 0.6/1kV FR-CV 2C-16㎟-P
X | #REF! | L-ELLV101-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 41 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-102 | 480V SWITCHGEAR | K-TF-342 K-TF-338 K-TF-328 K-TF-318 K-TF-314 K-TF-313 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-328; ROUTING PATH 4: K-TF-318; ROUTING PATH 5: K-TF-314; ROUTING PATH 6: K-TF-313 |  |  | L | ELLV101 | 02 | L-ELLV101-02 | ELLV101 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV201-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 38 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-202 | 480V SWITCHGEAR | K-TF-342 K-TF-338 K-TF-328 K-TF-321 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-328; ROUTING PATH 4: K-TF-321 |  |  | L | ELLV201 | 02 | L-ELLV201-02 | ELLV201 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV301-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 30 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-302 | 480V SWITCHGEAR | K-TF-342 K-TF-338 K-TF-333 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-333 |  |  | L | ELLV301 | 02 | L-ELLV301-02 | ELLV301 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV401-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 34 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-402 | 480V SWITCHGEAR | K-TF-342 K-TF-341 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-341 |  |  | L | ELLV401 | 02 | L-ELLV401-02 | ELLV401 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV501-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 25 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-502 | 480V SWITCHGEAR | K-TF-342 K-TF-341 K-TF-335 K-TF-323 K-TF-320 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-341; ROUTING PATH 3: K-TF-335; ROUTING PATH 4: K-TF-323; ROUTING PATH 5: K-TF-320 |  |  | L | ELLV501 | 02 | L-ELLV501-02 | ELLV501 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV601-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 29 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-602 | 480V SWITCHGEAR | K-TF-338 K-TF-333 K-TF-332 | ROUTING PATH 1: K-TF-338; ROUTING PATH 2: K-TF-333; ROUTING PATH 3: K-TF-332 |  |  | L | ELLV601 | 02 | L-ELLV601-02 | ELLV601 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV701-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 20 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-702 | 480V SWITCHGEAR | K-TF-342 K-TF-341 K-TF-340 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-341; ROUTING PATH 3: K-TF-340 |  |  | L | ELLV701 | 02 | L-ELLV701-02 | ELLV701 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV801-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 30 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-801 | 380/220V SWITCHGEAR | K-TF-342 K-TF-338 K-TF-328 K-TF-329 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-328; ROUTING PATH 4: K-TF-329 |  |  | L | ELLV801 | 02 | L-ELLV801-02 | ELLV801 | 0.6/1kV FR-CV 2C-4㎟-P
X | #REF! | L-ELLV901-02 | P | 0.6/1kV | FR-CV | 2C | 4 | 30 | 13 | 132.74 | - | - | 0.11 |  | F | 전기실 | EL-DP-002 | 110V DC DISTRIBUTION BOARD | 전기실 | EL-LV-901 | 380/220V SWITCHGEAR | K-TF-342 K-TF-338 K-TF-330 | ROUTING PATH 1: K-TF-342; ROUTING PATH 2: K-TF-338; ROUTING PATH 3: K-TF-330 |  |  | L | ELLV901 | 02 | L-ELLV901-02 | ELLV901 | 0.6/1kV FR-CV 2C-4㎟-P
X
X | #REF! | Control Cable
X | #REF! | T-ELHV001-01 | S | - | UL2919(RS485) | 2P | 24AWG | 52 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-HV-001 | 22.9kV SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TL-115; ROUTING PATH 2: X-TL-118; ROUTING PATH 3: X-TL-128; ROUTING PATH 4: X-TL-138; ROUTING PATH 5: X-TN-142; ROUTING PATH 6: X-TN-151; ROUTING PATH 7: X-TN-152; ROUTING PATH 8: X-TN-153 | PROTECTION RELAY | 190822 | T | ELHV001 | 01 | T-ELHV001-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELHV003-01 | S | - | UL2919(RS485) | 2P | 24AWG | 49 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-HV-003 | 22.9kV SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TL-115; ROUTING PATH 2: X-TL-118; ROUTING PATH 3: X-TL-128; ROUTING PATH 4: X-TL-138; ROUTING PATH 5: X-TN-142; ROUTING PATH 6: X-TN-151; ROUTING PATH 7: X-TN-152; ROUTING PATH 8: X-TN-153 | WHM | 190822 | T | ELHV003 | 01 | T-ELHV003-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X
X | #REF! | T-ELLV101-01 | S | - | UL2919(RS485) | 2P | 24AWG | 56 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-101 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-113 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TL-113; ROUTING PATH 2: X-TL-116; ROUTING PATH 3: X-TL-123; ROUTING PATH 4: X-TN-135; ROUTING PATH 5: X-TN-140; ROUTING PATH 6: X-TN-141; ROUTING PATH 7: X-TN-142; ROUTING PATH 8: X-TN-151; ROUTING PATH 9: X-TN-152; ROUTING PATH 10: X-TN-153 | PROTECTION RELAY | 190822 | T | ELLV101 | 01 | T-ELLV101-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV201-01 | S | - | UL2919(RS485) | 2P | 24AWG | 57 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-201 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-121 X-TL-128 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TL-121; ROUTING PATH 2: X-TL-128; ROUTING PATH 3: X-TN-142; ROUTING PATH 4: X-TN-151; ROUTING PATH 5: X-TN-152; ROUTING PATH 6: X-TN-153 | PROTECTION RELAY | 190822 | T | ELLV201 | 01 | T-ELLV201-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV301-01 | S | - | UL2919(RS485) | 2P | 24AWG | 43 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-301 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-133 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TL-133; ROUTING PATH 2: X-TL-138; ROUTING PATH 3: X-TN-142; ROUTING PATH 4: X-TN-151; ROUTING PATH 5: X-TN-152; ROUTING PATH 6: X-TN-153 | PROTECTION RELAY | 190822 | T | ELLV301 | 01 | T-ELLV301-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV401-01 | S | - | UL2919(RS485) | 2P | 24AWG | 47 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-401 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TN-141; ROUTING PATH 2: X-TN-142; ROUTING PATH 3: X-TN-151; ROUTING PATH 4: X-TN-152; ROUTING PATH 5: X-TN-153 | PROTECTION RELAY | 190822 | T | ELLV401 | 01 | T-ELLV401-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV501-01 | S | - | UL2919(RS485) | 2P | 24AWG | 37 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-501 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-120 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TL-120; ROUTING PATH 2: X-TL-123; ROUTING PATH 3: X-TN-135; ROUTING PATH 4: X-TN-140; ROUTING PATH 5: X-TN-141; ROUTING PATH 6: X-TN-142; ROUTING PATH 7: X-TN-151; ROUTING PATH 8: X-TN-152; ROUTING PATH 9: X-TN-153 | PROTECTION RELAY | 190822 | T | ELLV501 | 01 | T-ELLV501-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV601-01 | S | - | UL2919(RS485) | 2P | 24AWG | 42 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-601 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-132 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | ROUTING PATH 1: X-TL-132; ROUTING PATH 2: X-TN-135; ROUTING PATH 3: X-TN-140; ROUTING PATH 4: X-TN-141; ROUTING PATH 5: X-TN-142; ROUTING PATH 6: X-TN-151; ROUTING PATH 7: X-TN-152; ROUTING PATH 8: X-TN-153 | PROTECTION RELAY | 190822 | T | ELLV601 | 01 | T-ELLV601-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV701-01 | S | - | UL2919(RS485) | 2P | 24AWG | 33 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-701 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [13 empty] | PROTECTION RELAY | 190822 | T | ELLV701 | 01 | T-ELLV701-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV801-01 | S | - | UL2919(RS485) | 2P | 24AWG | 51 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-801 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-129 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-129 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | PROTECTION RELAY | 190822 | T | ELLV801 | 01 | T-ELLV801-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-ELLV901-01 | S | - | UL2919(RS485) | 2P | 24AWG | 51 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-LV-901 | LC SWGR | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-130 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-130 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [13 empty] | PROTECTION RELAY | 190822 | T | ELLV901 | 01 | T-ELLV901-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X
X | #REF! | C-ELHV001-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 52 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-001 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV001 | 02 | C-ELHV001-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 52 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-001 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 01 | C-INPLC002-01 | ELHV001 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV003-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 49 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-003 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV003 | 02 | C-ELHV003-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 49 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-003 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 02 | C-INPLC002-02 | ELHV003 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV004-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 48 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-004 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV004 | 01 | C-ELHV004-01 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-03 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 48 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-004 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 03 | C-INPLC002-03 | ELHV004 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV005-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 47 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-005 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV005 | 01 | C-ELHV005-01 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-04 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 47 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-005 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 04 | C-INPLC002-04 | ELHV005 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV006-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 46 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-006 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV006 | 01 | C-ELHV006-01 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-05 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 46 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-006 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 05 | C-INPLC002-05 | ELHV006 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV007-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 45 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-007 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV007 | 01 | C-ELHV007-01 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-06 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 45 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-007 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 06 | C-INPLC002-06 | ELHV007 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV008-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 45 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-008 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV008 | 01 | C-ELHV008-01 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-07 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 45 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-008 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 07 | C-INPLC002-07 | ELHV008 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV009-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 46 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-009 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-115 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-115 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV009 | 01 | C-ELHV009-01 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-08 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 46 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-009 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 08 | C-INPLC002-08 | ELHV009 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV010-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 47 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-010 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-114 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-114 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV010 | 01 | C-ELHV010-01 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-09 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 47 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-010 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-114 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-114 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 09 | C-INPLC002-09 | ELHV010 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV011-03 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 48 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-011 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-114 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-114 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELHV011 | 03 | C-ELHV011-03 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-10 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 48 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-011 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-114 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-114 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 10 | C-INPLC002-10 | ELHV011 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV012-03 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 48 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-012 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-114 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-114 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190827 | C | ELHV012 | 03 | C-ELHV012-03 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-11 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 48 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-012 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-114 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-114 | [11 empty] | COMMAND | 190827 | C | INPLC002 | 11 | C-INPLC002-11 | ELHV011 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV013-03 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 48 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-HV-013 | 22.9kV SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-114 L-TB-118 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-114 | L-TB-118 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190827 | C | ELHV013 | 03 | C-ELHV013-03 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-12 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 48 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-HV-013 | 22.9kV SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-114 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-114 | [11 empty] | COMMAND | 190827 | C | INPLC002 | 12 | C-INPLC002-12 | ELHV011 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X
X | #REF! | C-ELHV004-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 22 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-001 | 4MVA, 22.9-0.48V STEP-UP TR-1 | 전기실 | EL-HV-004 | 22.9kV SWGR | L-TB-113 L-TB-114 L-TB-115 | X-TN-140: L-TB-113; X-TN-141: L-TB-114; X-TN-142: L-TB-115 | [13 empty] | WTD |  | C | ELHV004 | 02 | C-ELHV004-02 | ELHV004 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV005-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 23 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-002 | 4.5MVA, 22.9-0.48V STEP-UP TR-2 | 전기실 | EL-HV-005 | 22.9kV SWGR | L-TB-129 L-TB-118 L-TB-115 | X-TN-140: L-TB-129; X-TN-141: L-TB-118; X-TN-142: L-TB-115 | [13 empty] | WTD |  | C | ELHV005 | 02 | C-ELHV005-02 | ELHV005 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV006-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 16 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-003 | 4.5MVA, 22.9-0.48V STEP-UP TR-3 | 전기실 | EL-HV-006 | 22.9kV SWGR | L-TB-128 L-TB-118 L-TB-115 | X-TN-140: L-TB-128; X-TN-141: L-TB-118; X-TN-142: L-TB-115 | [13 empty] | WTD |  | C | ELHV006 | 02 | C-ELHV006-02 | ELHV006 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV007-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 27 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-004 | 4.5MVA, 22.9-0.48V STEP-UP TR-4 | 전기실 | EL-HV-007 | 22.9kV SWGR | L-TD-142 L-TB-138 L-TB-128 L-TB-118 L-TB-115 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-118 | L-TB-115 | [14 empty] | WTD |  | C | ELHV007 | 02 | C-ELHV007-02 | ELHV007 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV008-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 20 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-005 | 4MVA, 22.9-0.48V STEP-UP TR-5 | 전기실 | EL-HV-008 | 22.9kV SWGR | L-TB-120 L-TB-121 L-TB-118 L-TB-115 | L-TB-120 | L-TB-121 | L-TB-118 | L-TB-115 | [15 empty] | WTD |  | C | ELHV008 | 02 | C-ELHV008-02 | ELHV008 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV009-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 31 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-006 | 4MVA, 22.9-0.48V STEP-UP TR-6 | 전기실 | EL-HV-009 | 22.9kV SWGR | L-TB-132 L-TB-128 L-TB-118 L-TB-115 | L-TB-132 | L-TB-128 | L-TB-118 | L-TB-115 | [15 empty] | WTD |  | C | ELHV009 | 02 | C-ELHV009-02 | ELHV009 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV010-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 27 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-007 | 4MVA, 22.9-0.48V STEP-UP TR-7 | 전기실 | EL-HV-010 | 22.9kV SWGR | L-TD-140 L-TD-141 L-TB-138 L-TB-128 L-TB-118 | L-TD-140 | L-TD-141 | L-TB-138 | L-TB-128 | L-TB-118 | [14 empty] | WTD |  | C | ELHV010 | 02 | C-ELHV010-02 | ELHV010 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV011-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 24 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-008 | 400kVA, 22.9-0.38/0.22V AUX TR-1 | 전기실 | EL-HV-011 | 22.9kV SWGR | L-TB-129 L-TB-118 L-TB-114 | X-TN-140: L-TB-129; X-TN-141: L-TB-118; X-TN-142: L-TB-114 | [13 empty] | WTD |  | C | ELHV011 | 02 | C-ELHV011-02 | ELHV011 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELHV012-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 24 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-009 | 400kVA, 22.9-0.38/0.22V AUX TR-2 | 전기실 | EL-HV-012 | 22.9kV SWGR | L-TB-130 L-TB-128 L-TB-118 L-TB-114 | L-TB-130 | L-TB-128 | L-TB-118 | L-TB-114 | [15 empty] | WTD |  | C | ELHV012 | 02 | C-ELHV012-02 | ELHV011 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X
X | #REF! | C-ELTR001-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 53 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-001 | 4MVA, 22.9-0.48V STEP-UP TR-1 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-113 L-TB-116 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-113 | L-TB-116 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [9 empty] | WTD | 190822 | C | ELTR001 | 01 | C-ELTR001-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR002-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 54 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-002 | 4.5MVA, 22.9-0.48V STEP-UP TR-2 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-129 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-129 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [12 empty] | WTD | 190822 | C | ELTR002 | 01 | C-ELTR002-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR003-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 40 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-003 | 4.5MVA, 22.9-0.48V STEP-UP TR-3 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [14 empty] | WTD | 190822 | C | ELTR003 | 01 | C-ELTR003-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR004-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 44 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-004 | 4.5MVA, 22.9-0.48V STEP-UP TR-4 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [15 empty] | WTD | 190822 | C | ELTR004 | 01 | C-ELTR004-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR005-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 34 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-005 | 4MVA, 22.9-0.48V STEP-UP TR-5 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-120 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-120 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [10 empty] | WTD | 190822 | C | ELTR005 | 01 | C-ELTR005-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR006-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 39 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-006 | 4MVA, 22.9-0.48V STEP-UP TR-6 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-132 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-132 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | WTD | 190822 | C | ELTR006 | 01 | C-ELTR006-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR007-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 30 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-007 | 4MVA, 22.9-0.48V STEP-UP TR-7 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | WTD | 190822 | C | ELTR007 | 01 | C-ELTR007-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR008-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 48 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-008 | 400kVA, 22.9-0.38/0.22V AUX TR-1 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-129 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-129 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [12 empty] | WTD | 190822 | C | ELTR008 | 01 | C-ELTR008-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELTR009-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 48 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-TR-009 | 400kVA, 22.9-0.38/0.22V AUX TR-2 | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-130 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-130 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | WTD | 190822 | C | ELTR009 | 01 | C-ELTR009-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X
X | #REF! | C-ELLV101-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 56 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-101 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-113 L-TB-116 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-113 | L-TB-116 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [9 empty] | STATUS (86) | 190822 | C | ELLV101 | 02 | C-ELLV101-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-13 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 56 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-101 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TD-141 L-TD-140 L-TB-135 L-TB-123 L-TB-116 L-TB-113 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TD-141 | L-TD-140 | L-TB-135 | L-TB-123 | L-TB-116 | L-TB-113 | [9 empty] | COMMAND | 190822 | C | INPLC002 | 13 | C-INPLC002-13 | ELLV101 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV201-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 57 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-201 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-129 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-129 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [12 empty] | STATUS (86) | 190822 | C | ELLV201 | 02 | C-ELLV201-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-14 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 57 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-201 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-129 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-129 | [12 empty] | COMMAND | 190822 | C | INPLC002 | 14 | C-INPLC002-14 | ELLV201 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV301-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 43 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-301 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-130 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-130 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | STATUS (86) | 190822 | C | ELLV301 | 02 | C-ELLV301-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-15 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 43 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-301 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-130 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-130 | [13 empty] | COMMAND | 190822 | C | INPLC002 | 15 | C-INPLC002-15 | ELLV301 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV401-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 47 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-401 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [15 empty] | STATUS (86) | 190822 | C | ELLV401 | 02 | C-ELLV401-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-16 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 47 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-401 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | [15 empty] | COMMAND | 190822 | C | INPLC002 | 16 | C-INPLC002-16 | ELLV401 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV501-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 37 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-501 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-120 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-120 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [10 empty] | STATUS (86) | 190822 | C | ELLV501 | 02 | C-ELLV501-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-17 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 37 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-501 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TD-141 L-TD-140 L-TB-135 L-TB-123 L-TB-120 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TD-141 | L-TD-140 | L-TB-135 | L-TB-123 | L-TB-120 | [10 empty] | COMMAND | 190822 | C | INPLC002 | 17 | C-INPLC002-17 | ELLV501 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV601-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 42 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-601 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-132 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-132 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | STATUS (86) | 190822 | C | ELLV601 | 02 | C-ELLV601-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-18 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 42 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-601 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TD-141 L-TD-140 L-TB-135 L-TB-132 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TD-141 | L-TD-140 | L-TB-135 | L-TB-132 | [11 empty] | COMMAND | 190822 | C | INPLC002 | 18 | C-INPLC002-18 | ELLV601 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV701-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 33 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-701 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | STATUS (86) | 190822 | C | ELLV701 | 02 | C-ELLV701-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-19 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 33 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-701 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TD-141 L-TD-140 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TD-141 | L-TD-140 | [13 empty] | COMMAND | 190822 | C | INPLC002 | 19 | C-INPLC002-19 | ELLV701 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV801-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 51 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-801 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-129 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-129 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [12 empty] | STATUS (86) | 190822 | C | ELLV801 | 02 | C-ELLV801-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-20 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 51 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-801 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-128 L-TB-129 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-128 | L-TB-129 | [12 empty] | COMMAND | 190822 | C | INPLC002 | 20 | C-INPLC002-20 | ELLV801 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELLV901-02 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 51 | 20.5 | 330.07 | - | - |  |  |  | 전기실 | EL-LV-901 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-130 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-130 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | STATUS (86) | 190822 | C | ELLV901 | 02 | C-ELLV901-02 | INPLC002 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | C-INPLC002-21 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 51 | 14.5 | 165.13 | - | - |  |  |  | 전자기기실 | IN-PLC-002 | PLC PANEL | 전기실 | EL-LV-901 | LC SWGR | L-TD-153 L-TD-152 L-TD-151 L-TD-142 L-TB-138 L-TB-130 | L-TD-153 | L-TD-152 | L-TD-151 | L-TD-142 | L-TB-138 | L-TB-130 | [13 empty] | COMMAND | 190822 | C | INPLC002 | 21 | C-INPLC002-21 | ELLV801 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X
X | #REF! | C-ELLV102-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 57 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-102 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-113 L-TB-116 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-113 | L-TB-116 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [9 empty] | COMMON FAULT ALARM | 190827 | C | ELLV102 | 01 | C-ELLV102-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV103-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 58 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-103 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-113 L-TB-116 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-113 | L-TB-116 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [9 empty] | COMMON FAULT ALARM | 190827 | C | ELLV103 | 01 | C-ELLV103-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV202-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 58 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-202 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-121 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-121 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [12 empty] | COMMON FAULT ALARM | 190827 | C | ELLV202 | 01 | C-ELLV202-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV203-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 59 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-203 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-121 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-121 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [12 empty] | COMMON FAULT ALARM | 190827 | C | ELLV203 | 01 | C-ELLV203-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV302-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 44 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-302 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-133 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-133 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | COMMON FAULT ALARM | 190827 | C | ELLV302 | 01 | C-ELLV302-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV303-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 45 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-303 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-133 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-133 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | COMMON FAULT ALARM | 190827 | C | ELLV303 | 01 | C-ELLV303-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV402-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 48 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-402 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [14 empty] | COMMON FAULT ALARM | 190827 | C | ELLV402 | 01 | C-ELLV402-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV403-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 49 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-403 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [14 empty] | COMMON FAULT ALARM | 190827 | C | ELLV403 | 01 | C-ELLV403-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV502-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 38 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-502 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-120 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-120 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [10 empty] | COMMON FAULT ALARM | 190827 | C | ELLV502 | 01 | C-ELLV502-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV503-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 39 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-503 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-120 L-TB-123 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-120 | L-TB-123 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [10 empty] | COMMON FAULT ALARM | 190827 | C | ELLV503 | 01 | C-ELLV503-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV602-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 43 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-602 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-132 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-132 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | COMMON FAULT ALARM | 190827 | C | ELLV602 | 01 | C-ELLV602-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV603-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 44 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-603 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-132 L-TB-135 L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-132 | L-TB-135 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [11 empty] | COMMON FAULT ALARM | 190827 | C | ELLV603 | 01 | C-ELLV603-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV702-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 34 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-702 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | COMMON FAULT ALARM | 190827 | C | ELLV702 | 01 | C-ELLV702-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV703-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 35 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-703 | LC SWGR | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-140 L-TD-141 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TD-140 | L-TD-141 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | COMMON FAULT ALARM | 190827 | C | ELLV703 | 01 | C-ELLV703-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV802-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 57 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-129 L-TB-128 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-129 | L-TB-128 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [12 empty] | COMMON FAULT ALARM | 190827 | C | ELLV802 | 01 | C-ELLV802-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELLV902-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 57 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TB-130 L-TB-138 L-TD-142 L-TD-151 L-TD-152 L-TD-153 | L-TB-130 | L-TB-138 | L-TD-142 | L-TD-151 | L-TD-152 | L-TD-153 | [13 empty] | COMMON FAULT ALARM | 190827 | C | ELLV902 | 01 | C-ELLV902-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X
X | #REF! | T-ELUPSBC001-01 | S | - | UL2919(RS485) | 2P | 24AWG | 25 | 9 | 63.62 | - | - |  |  |  | 전기실 | EL-UPS&BC-001 | UPS & BC PANEL | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TN-151 X-TN-152 X-TN-153 | L-TD-140 L-TD-140: X-TN-151; L-TD-141 L-TD-141: X-TN-152; L-TD-142 L-TD-142: X-TN-153 | [14 empty] | 191022 | T | ELUPSBC001 | 01 | T-ELUPSBC001-01 | INPLC002 | - UL2919(RS485) 2P-24AWG㎟-S
X
X | #REF! | C-ELAVR001-02 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 26 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-AVR-001 | AVR PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AC INPUT MCCB-1 ON / FAULT STATUS | 190822 | C | ELAVR001 | 02 | C-ELAVR001-02 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELAVR001-03 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 26 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-AVR-001 | AVR PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AC OUTPUT MCCB-1 ON / FAULT STATUS | 190822 | C | ELAVR001 | 03 | C-ELAVR001-03 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELAVR001-04 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 26 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-AVR-001 | AVR PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AVR VOLTAGE UVR(27) ALARM | 190822 | C | ELAVR001 | 04 | C-ELAVR001-04 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELAVR001-05 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 26 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-AVR-001 | AVR PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AVR VOLTAGE OVR(59) ALARM | 190822 | C | ELAVR001 | 05 | C-ELAVR001-05 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELAVR001-06 | S | 0.6/1kV | FR-CVV-I/C AMS | 2P | 1.5 | 26 | 16 | 201.07 | - | - |  |  |  | 전기실 | EL-AVR-001 | AVR PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AC INPUT VOLTAGE | 190822 | C | ELAVR001 | 06 | C-ELAVR001-06 | INPLC002 | 0.6/1kV FR-CVV-I/C AMS 2P-1.5㎟-S
X | #REF! | C-ELAVR001-07 | S | 0.6/1kV | FR-CVV-I/C AMS | 2P | 1.5 | 26 | 16 | 201.07 | - | - |  |  |  | 전기실 | EL-AVR-001 | AVR PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AC OUTPUT CURRENT | 190822 | C | ELAVR001 | 07 | C-ELAVR001-07 | INPLC002 | 0.6/1kV FR-CVV-I/C AMS 2P-1.5㎟-S
X | #REF! | C-ELAVR001-08 | S | 0.6/1kV | FR-CVV-I/C AMS | 2P | 1.5 | 26 | 16 | 201.07 | - | - |  |  |  | 전기실 | EL-AVR-001 | AVR PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AC OUTPUT VOLTAGE | 190822 | C | ELAVR001 | 08 | C-ELAVR001-08 | INPLC002 | 0.6/1kV FR-CVV-I/C AMS 2P-1.5㎟-S
X | #REF! | C-ELDP001-04 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 25 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-DP-001 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | MAIN MCCB-100 ON / FAULT STATUS | 190822 | C | ELDP001 | 04 | C-ELDP001-04 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELDP001-05 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 25 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-DP-001 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | VOLTAGE UVR(27) ALARM | 190822 | C | ELDP001 | 05 | C-ELDP001-05 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELDP001-06 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 25 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-DP-001 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | VOLTAGE OVR(59) ALARM | 190822 | C | ELDP001 | 06 | C-ELDP001-06 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELDP001-07 | S | 0.6/1kV | FR-CVV-I/C AMS | 2P | 1.5 | 25 | 16 | 201.07 | - | - |  |  |  | 전기실 | EL-DP-001 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | AC OUTPUT VOLTAGE | 190822 | C | ELDP001 | 07 | C-ELDP001-07 | INPLC002 | 0.6/1kV FR-CVV-I/C AMS 2P-1.5㎟-S
X | #REF! | C-ELDP002-01 | C | 0.6/1kV | FR-CVV-S | 4C | 2.5 | 25 | 14.5 | 165.13 | - | - |  |  |  | 전기실 | EL-DP-002 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | MAIN MCCB-100 ON / FAULT STATUS | 190822 | C | ELDP002 | 01 | C-ELDP002-01 | INPLC002 | 0.6/1kV FR-CVV-S 4C-2.5㎟-C
X | #REF! | C-ELDP002-02 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 25 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-DP-002 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | DC UNDERVOLTAGE RELAY(27D) ALARM | 190822 | C | ELDP002 | 02 | C-ELDP002-02 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELDP002-03 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 25 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-DP-002 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | DC OVERVOLTAGE RELAY(59D) ALARM | 190822 | C | ELDP002 | 03 | C-ELDP002-03 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELDP002-04 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 25 | 13.5 | 143.14 | - | - |  |  |  | 전기실 | EL-DP-002 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | DC GROUND RELAY(64D) ALARM | 190822 | C | ELDP002 | 04 | C-ELDP002-04 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELDP002-05 | S | 0.6/1kV | FR-CVV-I/C AMS | 2P | 1.5 | 25 | 16 | 201.07 | - | - |  |  |  | 전기실 | EL-DP-002 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | DC DIST. OUTPUT CURRENT | 190822 | C | ELDP002 | 05 | C-ELDP002-05 | INPLC002 | 0.6/1kV FR-CVV-I/C AMS 2P-1.5㎟-S
X | #REF! | C-ELDP002-06 | S | 0.6/1kV | FR-CVV-I/C AMS | 2P | 1.5 | 25 | 16 | 201.07 | - | - |  |  |  | 전기실 | EL-DP-002 | UPS DP PANEL | 전자기기실 | IN-PLC-002 | PLC PANEL | L-TD-151 L-TD-152 L-TD-153 | L-TD-140 L-TD-140: L-TD-151; L-TD-141 L-TD-141: L-TD-152; L-TD-142 L-TD-142: L-TD-153 | [13 empty] | DC DIST. OUTPUT VOLTAGE | 190822 | C | ELDP002 | 06 | C-ELDP002-06 | INPLC002 | 0.6/1kV FR-CVV-I/C AMS 2P-1.5㎟-S
X
X | #REF! | C-ELHF001-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 95 | 13.5 | 143.14 | X-PA-181 | 4 |  |  |  | FUEL CELL AREA | EL-HF-001 | EHT PNL | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-113 X-TL-114 X-TL-118 X-TL-128 X-TL-139 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-113 | X-TL-114 | X-TL-118 | X-TL-128 | X-TL-139 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | TOTAL FAULT STATUS | 190822 | C | ELHF001 | 01 | C-ELHF001-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X | #REF! | C-ELHF002-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 120 | 13.5 | 143.14 | X-PA-371 | 4 |  |  |  | FUEL CELL AREA | EL-HF-002 | EHT PNL | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [11 empty] | TOTAL FAULT STATUS | 190822 | C | ELHF002 | 01 | C-ELHF002-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X
X | #REF! | C-FFFA001-01 | C | 0.6/1kV | FR-CVV-S | 3C | 2.5 | 15 | 13.5 | 143.14 | - | 4 |  |  |  | FUEL CELL AREA | FF-FA-001 | 소방수신반 | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-154 X-TN-153 | L-TD-140 L-TD-140: X-TL-154; L-TD-141 L-TD-141: X-TN-153 | [14 empty] | 190822 | C | FFFA001 | 01 | C-FFFA001-01 | INPLC002 | 0.6/1kV FR-CVV-S 3C-2.5㎟-C
X
X | #REF! | Communication & Fire Alarm Cable
X | #REF! | T-SOFC101-01 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | X-PA-901 | 8 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | - | [21 empty] | T | SOFC101 | 01 | T-SOFC101-01 | SOFC101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC101-02 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | - | [21 empty] | T | SOFC101 | 02 | T-SOFC101-02 | SOFC101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC101-03 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | - | [21 empty] | T | SOFC101 | 03 | T-SOFC101-03 | SOFC101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC101-04 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | - | [21 empty] | T | SOFC101 | 04 | T-SOFC101-04 | SOFC101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC101-05 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #101 | FUEL CELL #101 | - | [21 empty] | T | SOFC101 | 05 | T-SOFC101-05 | SOFC101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC102-01 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | X-PA-902 | 12 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | - | [21 empty] | T | SOFC102 | 01 | T-SOFC102-01 | SOFC102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC102-02 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | - | [21 empty] | T | SOFC102 | 02 | T-SOFC102-02 | SOFC102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC102-03 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | - | [21 empty] | T | SOFC102 | 03 | T-SOFC102-03 | SOFC102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC102-04 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | - | [21 empty] | T | SOFC102 | 04 | T-SOFC102-04 | SOFC102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC102-05 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #102 | FUEL CELL #102 | - | [21 empty] | T | SOFC102 | 05 | T-SOFC102-05 | SOFC102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC103-01 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | X-PA-903 | 14 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | - | [21 empty] | T | SOFC103 | 01 | T-SOFC103-01 | SOFC103 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC103-02 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | - | [21 empty] | T | SOFC103 | 02 | T-SOFC103-02 | SOFC103 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC103-03 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | - | [21 empty] | T | SOFC103 | 03 | T-SOFC103-03 | SOFC103 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC103-04 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | - | [21 empty] | T | SOFC103 | 04 | T-SOFC103-04 | SOFC103 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC103-05 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #103 | FUEL CELL #103 | - | [21 empty] | T | SOFC103 | 05 | T-SOFC103-05 | SOFC103 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC104-01 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | X-PA-904 | 19 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | - | [21 empty] | T | SOFC104 | 01 | T-SOFC104-01 | SOFC104 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC104-02 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | - | [21 empty] | T | SOFC104 | 02 | T-SOFC104-02 | SOFC104 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC104-03 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | - | [21 empty] | T | SOFC104 | 03 | T-SOFC104-03 | SOFC104 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC104-04 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | - | [21 empty] | T | SOFC104 | 04 | T-SOFC104-04 | SOFC104 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC104-05 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #104 | FUEL CELL #104 | - | [21 empty] | T | SOFC104 | 05 | T-SOFC104-05 | SOFC104 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC105-01 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | X-PA-905 | 21 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | - | [21 empty] | T | SOFC105 | 01 | T-SOFC105-01 | SOFC105 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC105-02 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | - | [21 empty] | T | SOFC105 | 02 | T-SOFC105-02 | SOFC105 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC105-03 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | - | [21 empty] | T | SOFC105 | 03 | T-SOFC105-03 | SOFC105 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC105-04 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | - | [21 empty] | T | SOFC105 | 04 | T-SOFC105-04 | SOFC105 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC105-05 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #105 | FUEL CELL #105 | - | [21 empty] | T | SOFC105 | 05 | T-SOFC105-05 | SOFC105 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC106-01 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | X-PA-906 | 26 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | - | [21 empty] | T | SOFC106 | 01 | T-SOFC106-01 | SOFC106 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC106-02 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | - | [21 empty] | T | SOFC106 | 02 | T-SOFC106-02 | SOFC106 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC106-03 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | - | [21 empty] | T | SOFC106 | 03 | T-SOFC106-03 | SOFC106 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC106-04 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | - | [21 empty] | T | SOFC106 | 04 | T-SOFC106-04 | SOFC106 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC106-05 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #106 | FUEL CELL #106 | - | [21 empty] | T | SOFC106 | 05 | T-SOFC106-05 | SOFC106 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC107-01 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | X-PA-907 | 28 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | - | [21 empty] | T | SOFC107 | 01 | T-SOFC107-01 | SOFC107 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC107-02 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | - | [21 empty] | T | SOFC107 | 02 | T-SOFC107-02 | SOFC107 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC107-03 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | - | [21 empty] | T | SOFC107 | 03 | T-SOFC107-03 | SOFC107 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC107-04 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | - | [21 empty] | T | SOFC107 | 04 | T-SOFC107-04 | SOFC107 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC107-05 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #107 | FUEL CELL #107 | - | [21 empty] | T | SOFC107 | 05 | T-SOFC107-05 | SOFC107 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC108-01 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | X-PA-908 | 32 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | - | [21 empty] | T | SOFC108 | 01 | T-SOFC108-01 | SOFC108 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC108-02 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | - | [21 empty] | T | SOFC108 | 02 | T-SOFC108-02 | SOFC108 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC108-03 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | - | [21 empty] | T | SOFC108 | 03 | T-SOFC108-03 | SOFC108 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC108-04 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | - | [21 empty] | T | SOFC108 | 04 | T-SOFC108-04 | SOFC108 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC108-05 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #108 | FUEL CELL #108 | - | [21 empty] | T | SOFC108 | 05 | T-SOFC108-05 | SOFC108 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC109-01 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | X-PA-909 | 34 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | - | [21 empty] | T | SOFC109 | 01 | T-SOFC109-01 | SOFC109 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC109-02 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | - | [21 empty] | T | SOFC109 | 02 | T-SOFC109-02 | SOFC109 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC109-03 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | - | [21 empty] | T | SOFC109 | 03 | T-SOFC109-03 | SOFC109 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC109-04 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | - | [21 empty] | T | SOFC109 | 04 | T-SOFC109-04 | SOFC109 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC109-05 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | SOFC #109 | FUEL CELL #109 | - | [21 empty] | T | SOFC109 | 05 | T-SOFC109-05 | SOFC109 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM101-01 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | X-PA-910 | 8 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | WDM #101 | WATER DISTRIBUTION MODULE #101 | - | [21 empty] | T | WDM101 | 01 | T-WDM101-01 | WDM101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM101-02 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | WDM #101 | WATER DISTRIBUTION MODULE #101 | - | [21 empty] | T | WDM101 | 02 | T-WDM101-02 | WDM101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM101-03 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | WDM #101 | WATER DISTRIBUTION MODULE #101 | - | [21 empty] | T | WDM101 | 03 | T-WDM101-03 | WDM101 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM102-01 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | X-PA-911 | 6 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | WDM #102 | WATER DISTRIBUTION MODULE #102 | - | [21 empty] | T | WDM102 | 01 | T-WDM102-01 | WDM102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM102-02 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | WDM #102 | WATER DISTRIBUTION MODULE #102 | - | [21 empty] | T | WDM102 | 02 | T-WDM102-02 | WDM102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM102-03 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | WDM #102 | WATER DISTRIBUTION MODULE #102 | - | [21 empty] | T | WDM102 | 03 | T-WDM102-03 | WDM102 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC201-01 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | X-PA-912 | 8 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | - | [21 empty] | T | SOFC201 | 01 | T-SOFC201-01 | SOFC201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC201-02 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | - | [21 empty] | T | SOFC201 | 02 | T-SOFC201-02 | SOFC201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC201-03 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | - | [21 empty] | T | SOFC201 | 03 | T-SOFC201-03 | SOFC201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC201-04 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | - | [21 empty] | T | SOFC201 | 04 | T-SOFC201-04 | SOFC201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC201-05 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #201 | FUEL CELL #201 | - | [21 empty] | T | SOFC201 | 05 | T-SOFC201-05 | SOFC201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC202-01 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | X-PA-913 | 10 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | - | [21 empty] | T | SOFC202 | 01 | T-SOFC202-01 | SOFC202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC202-02 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | - | [21 empty] | T | SOFC202 | 02 | T-SOFC202-02 | SOFC202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC202-03 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | - | [21 empty] | T | SOFC202 | 03 | T-SOFC202-03 | SOFC202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC202-04 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | - | [21 empty] | T | SOFC202 | 04 | T-SOFC202-04 | SOFC202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC202-05 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #202 | FUEL CELL #202 | - | [21 empty] | T | SOFC202 | 05 | T-SOFC202-05 | SOFC202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC203-01 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | X-PA-914 | 14 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | - | [21 empty] | T | SOFC203 | 01 | T-SOFC203-01 | SOFC203 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC203-02 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | - | [21 empty] | T | SOFC203 | 02 | T-SOFC203-02 | SOFC203 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC203-03 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | - | [21 empty] | T | SOFC203 | 03 | T-SOFC203-03 | SOFC203 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC203-04 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | - | [21 empty] | T | SOFC203 | 04 | T-SOFC203-04 | SOFC203 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC203-05 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #203 | FUEL CELL #203 | - | [21 empty] | T | SOFC203 | 05 | T-SOFC203-05 | SOFC203 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC204-01 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | X-PA-915 | 16 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | - | [21 empty] | T | SOFC204 | 01 | T-SOFC204-01 | SOFC204 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC204-02 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | - | [21 empty] | T | SOFC204 | 02 | T-SOFC204-02 | SOFC204 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC204-03 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | - | [21 empty] | T | SOFC204 | 03 | T-SOFC204-03 | SOFC204 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC204-04 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | - | [21 empty] | T | SOFC204 | 04 | T-SOFC204-04 | SOFC204 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC204-05 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #204 | FUEL CELL #204 | - | [21 empty] | T | SOFC204 | 05 | T-SOFC204-05 | SOFC204 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC205-01 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | X-PA-916 | 21 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | - | [21 empty] | T | SOFC205 | 01 | T-SOFC205-01 | SOFC205 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC205-02 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | - | [21 empty] | T | SOFC205 | 02 | T-SOFC205-02 | SOFC205 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC205-03 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | - | [21 empty] | T | SOFC205 | 03 | T-SOFC205-03 | SOFC205 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC205-04 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | - | [21 empty] | T | SOFC205 | 04 | T-SOFC205-04 | SOFC205 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC205-05 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #205 | FUEL CELL #205 | - | [21 empty] | T | SOFC205 | 05 | T-SOFC205-05 | SOFC205 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC206-01 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | X-PA-917 | 23 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | - | [21 empty] | T | SOFC206 | 01 | T-SOFC206-01 | SOFC206 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC206-02 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | - | [21 empty] | T | SOFC206 | 02 | T-SOFC206-02 | SOFC206 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC206-03 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | - | [21 empty] | T | SOFC206 | 03 | T-SOFC206-03 | SOFC206 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC206-04 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | - | [21 empty] | T | SOFC206 | 04 | T-SOFC206-04 | SOFC206 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC206-05 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #206 | FUEL CELL #206 | - | [21 empty] | T | SOFC206 | 05 | T-SOFC206-05 | SOFC206 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC207-01 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | X-PA-918 | 28 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | - | [21 empty] | T | SOFC207 | 01 | T-SOFC207-01 | SOFC207 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC207-02 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | - | [21 empty] | T | SOFC207 | 02 | T-SOFC207-02 | SOFC207 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC207-03 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | - | [21 empty] | T | SOFC207 | 03 | T-SOFC207-03 | SOFC207 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC207-04 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | - | [21 empty] | T | SOFC207 | 04 | T-SOFC207-04 | SOFC207 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC207-05 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #207 | FUEL CELL #207 | - | [21 empty] | T | SOFC207 | 05 | T-SOFC207-05 | SOFC207 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC208-01 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | X-PA-919 | 30 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | - | [21 empty] | T | SOFC208 | 01 | T-SOFC208-01 | SOFC208 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC208-02 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | - | [21 empty] | T | SOFC208 | 02 | T-SOFC208-02 | SOFC208 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC208-03 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | - | [21 empty] | T | SOFC208 | 03 | T-SOFC208-03 | SOFC208 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC208-04 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | - | [21 empty] | T | SOFC208 | 04 | T-SOFC208-04 | SOFC208 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC208-05 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #208 | FUEL CELL #208 | - | [21 empty] | T | SOFC208 | 05 | T-SOFC208-05 | SOFC208 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC209-01 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | X-PA-920 | 34 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | - | [21 empty] | T | SOFC209 | 01 | T-SOFC209-01 | SOFC209 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC209-02 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | - | [21 empty] | T | SOFC209 | 02 | T-SOFC209-02 | SOFC209 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC209-03 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | - | [21 empty] | T | SOFC209 | 03 | T-SOFC209-03 | SOFC209 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC209-04 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | - | [21 empty] | T | SOFC209 | 04 | T-SOFC209-04 | SOFC209 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC209-05 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #209 | FUEL CELL #209 | - | [21 empty] | T | SOFC209 | 05 | T-SOFC209-05 | SOFC209 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC210-01 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | X-PA-921 | 36 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | - | [21 empty] | T | SOFC210 | 01 | T-SOFC210-01 | SOFC210 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC210-02 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | - | [21 empty] | T | SOFC210 | 02 | T-SOFC210-02 | SOFC210 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC210-03 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | - | [21 empty] | T | SOFC210 | 03 | T-SOFC210-03 | SOFC210 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC210-04 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | - | [21 empty] | T | SOFC210 | 04 | T-SOFC210-04 | SOFC210 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC210-05 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | SOFC #210 | FUEL CELL #210 | - | [21 empty] | T | SOFC210 | 05 | T-SOFC210-05 | SOFC210 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM201-01 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | X-PA-922 | 8 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | WDM #201 | WATER DISTRIBUTION MODULE #201 | - | [21 empty] | T | WDM201 | 01 | T-WDM201-01 | WDM201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM201-02 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | WDM #201 | WATER DISTRIBUTION MODULE #201 | - | [21 empty] | T | WDM201 | 02 | T-WDM201-02 | WDM201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM201-03 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | WDM #201 | WATER DISTRIBUTION MODULE #201 | - | [21 empty] | T | WDM201 | 03 | T-WDM201-03 | WDM201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM202-01 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | X-PA-923 | 6 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | WDM #202 | WATER DISTRIBUTION MODULE #202 | - | [21 empty] | T | WDM202 | 01 | T-WDM202-01 | WDM202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM202-02 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | WDM #202 | WATER DISTRIBUTION MODULE #202 | - | [21 empty] | T | WDM202 | 02 | T-WDM202-02 | WDM202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM202-03 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | WDM #202 | WATER DISTRIBUTION MODULE #202 | - | [21 empty] | T | WDM202 | 03 | T-WDM202-03 | WDM202 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC301-01 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | X-PA-924 | 8 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | - | [21 empty] | T | SOFC301 | 01 | T-SOFC301-01 | SOFC301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC301-02 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | - | [21 empty] | T | SOFC301 | 02 | T-SOFC301-02 | SOFC301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC301-03 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | - | [21 empty] | T | SOFC301 | 03 | T-SOFC301-03 | SOFC301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC301-04 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | - | [21 empty] | T | SOFC301 | 04 | T-SOFC301-04 | SOFC301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC301-05 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #301 | FUEL CELL #301 | - | [21 empty] | T | SOFC301 | 05 | T-SOFC301-05 | SOFC301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC302-01 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | X-PA-925 | 10 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | - | [21 empty] | T | SOFC302 | 01 | T-SOFC302-01 | SOFC302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC302-02 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | - | [21 empty] | T | SOFC302 | 02 | T-SOFC302-02 | SOFC302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC302-03 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | - | [21 empty] | T | SOFC302 | 03 | T-SOFC302-03 | SOFC302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC302-04 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | - | [21 empty] | T | SOFC302 | 04 | T-SOFC302-04 | SOFC302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC302-05 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #302 | FUEL CELL #302 | - | [21 empty] | T | SOFC302 | 05 | T-SOFC302-05 | SOFC302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC303-01 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | X-PA-926 | 14 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | - | [21 empty] | T | SOFC303 | 01 | T-SOFC303-01 | SOFC303 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC303-02 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | - | [21 empty] | T | SOFC303 | 02 | T-SOFC303-02 | SOFC303 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC303-03 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | - | [21 empty] | T | SOFC303 | 03 | T-SOFC303-03 | SOFC303 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC303-04 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | - | [21 empty] | T | SOFC303 | 04 | T-SOFC303-04 | SOFC303 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC303-05 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #303 | FUEL CELL #303 | - | [21 empty] | T | SOFC303 | 05 | T-SOFC303-05 | SOFC303 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC304-01 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | X-PA-927 | 16 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | - | [21 empty] | T | SOFC304 | 01 | T-SOFC304-01 | SOFC304 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC304-02 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | - | [21 empty] | T | SOFC304 | 02 | T-SOFC304-02 | SOFC304 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC304-03 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | - | [21 empty] | T | SOFC304 | 03 | T-SOFC304-03 | SOFC304 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC304-04 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | - | [21 empty] | T | SOFC304 | 04 | T-SOFC304-04 | SOFC304 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC304-05 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #304 | FUEL CELL #304 | - | [21 empty] | T | SOFC304 | 05 | T-SOFC304-05 | SOFC304 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC305-01 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | X-PA-928 | 21 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | - | [21 empty] | T | SOFC305 | 01 | T-SOFC305-01 | SOFC305 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC305-02 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | - | [21 empty] | T | SOFC305 | 02 | T-SOFC305-02 | SOFC305 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC305-03 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | - | [21 empty] | T | SOFC305 | 03 | T-SOFC305-03 | SOFC305 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC305-04 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | - | [21 empty] | T | SOFC305 | 04 | T-SOFC305-04 | SOFC305 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC305-05 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #305 | FUEL CELL #305 | - | [21 empty] | T | SOFC305 | 05 | T-SOFC305-05 | SOFC305 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC306-01 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | X-PA-929 | 23 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | - | [21 empty] | T | SOFC306 | 01 | T-SOFC306-01 | SOFC306 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC306-02 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | - | [21 empty] | T | SOFC306 | 02 | T-SOFC306-02 | SOFC306 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC306-03 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | - | [21 empty] | T | SOFC306 | 03 | T-SOFC306-03 | SOFC306 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC306-04 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | - | [21 empty] | T | SOFC306 | 04 | T-SOFC306-04 | SOFC306 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC306-05 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #306 | FUEL CELL #306 | - | [21 empty] | T | SOFC306 | 05 | T-SOFC306-05 | SOFC306 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC307-01 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | X-PA-930 | 28 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | - | [21 empty] | T | SOFC307 | 01 | T-SOFC307-01 | SOFC307 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC307-02 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | - | [21 empty] | T | SOFC307 | 02 | T-SOFC307-02 | SOFC307 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC307-03 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | - | [21 empty] | T | SOFC307 | 03 | T-SOFC307-03 | SOFC307 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC307-04 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | - | [21 empty] | T | SOFC307 | 04 | T-SOFC307-04 | SOFC307 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC307-05 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #307 | FUEL CELL #307 | - | [21 empty] | T | SOFC307 | 05 | T-SOFC307-05 | SOFC307 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC308-01 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | X-PA-931 | 30 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | - | [21 empty] | T | SOFC308 | 01 | T-SOFC308-01 | SOFC308 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC308-02 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | - | [21 empty] | T | SOFC308 | 02 | T-SOFC308-02 | SOFC308 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC308-03 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | - | [21 empty] | T | SOFC308 | 03 | T-SOFC308-03 | SOFC308 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC308-04 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | - | [21 empty] | T | SOFC308 | 04 | T-SOFC308-04 | SOFC308 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC308-05 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #308 | FUEL CELL #308 | - | [21 empty] | T | SOFC308 | 05 | T-SOFC308-05 | SOFC308 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC309-01 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | X-PA-924 | 34 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | - | [21 empty] | T | SOFC309 | 01 | T-SOFC309-01 | SOFC309 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC309-02 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | - | [21 empty] | T | SOFC309 | 02 | T-SOFC309-02 | SOFC309 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC309-03 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | - | [21 empty] | T | SOFC309 | 03 | T-SOFC309-03 | SOFC309 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC309-04 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | - | [21 empty] | T | SOFC309 | 04 | T-SOFC309-04 | SOFC309 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC309-05 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #309 | FUEL CELL #309 | - | [21 empty] | T | SOFC309 | 05 | T-SOFC309-05 | SOFC309 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC310-01 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | X-PA-924 | 36 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | - | [21 empty] | T | SOFC310 | 01 | T-SOFC310-01 | SOFC310 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC310-02 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | - | [21 empty] | T | SOFC310 | 02 | T-SOFC310-02 | SOFC310 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC310-03 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | - | [21 empty] | T | SOFC310 | 03 | T-SOFC310-03 | SOFC310 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC310-04 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | - | [21 empty] | T | SOFC310 | 04 | T-SOFC310-04 | SOFC310 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC310-05 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | SOFC #310 | FUEL CELL #310 | - | [21 empty] | T | SOFC310 | 05 | T-SOFC310-05 | SOFC310 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM301-01 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | X-PA-925 | 8 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | WDM #301 | WATER DISTRIBUTION MODULE #301 | - | [21 empty] | T | WDM301 | 01 | T-WDM301-01 | WDM301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM301-02 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | WDM #301 | WATER DISTRIBUTION MODULE #301 | - | [21 empty] | T | WDM301 | 02 | T-WDM301-02 | WDM301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM301-03 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | WDM #301 | WATER DISTRIBUTION MODULE #301 | - | [21 empty] | T | WDM301 | 03 | T-WDM301-03 | WDM301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM302-01 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | X-PA-926 | 6 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | WDM #302 | WATER DISTRIBUTION MODULE #302 | - | [21 empty] | T | WDM302 | 01 | T-WDM302-01 | WDM302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM302-02 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | WDM #302 | WATER DISTRIBUTION MODULE #302 | - | [21 empty] | T | WDM302 | 02 | T-WDM302-02 | WDM302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM302-03 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #301 | TELE CABINET #301 | FUEL CELL AREA | WDM #302 | WATER DISTRIBUTION MODULE #302 | - | [21 empty] | T | WDM302 | 03 | T-WDM302-03 | WDM302 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC401-01 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | X-PA-927 | 8 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | - | [21 empty] | T | SOFC401 | 01 | T-SOFC401-01 | SOFC401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC401-02 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | - | [21 empty] | T | SOFC401 | 02 | T-SOFC401-02 | SOFC401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC401-03 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | - | [21 empty] | T | SOFC401 | 03 | T-SOFC401-03 | SOFC401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC401-04 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | - | [21 empty] | T | SOFC401 | 04 | T-SOFC401-04 | SOFC401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC401-05 | C |  | STP-CAT.5e | 4P | 24AWG | 10 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #401 | FUEL CELL #401 | - | [21 empty] | T | SOFC401 | 05 | T-SOFC401-05 | SOFC401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC402-01 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | X-PA-928 | 10 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | - | [21 empty] | T | SOFC402 | 01 | T-SOFC402-01 | SOFC402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC402-02 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | - | [21 empty] | T | SOFC402 | 02 | T-SOFC402-02 | SOFC402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC402-03 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | - | [21 empty] | T | SOFC402 | 03 | T-SOFC402-03 | SOFC402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC402-04 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | - | [21 empty] | T | SOFC402 | 04 | T-SOFC402-04 | SOFC402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC402-05 | C |  | STP-CAT.5e | 4P | 24AWG | 17 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #402 | FUEL CELL #402 | - | [21 empty] | T | SOFC402 | 05 | T-SOFC402-05 | SOFC402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC403-01 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | X-PA-929 | 14 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | - | [21 empty] | T | SOFC403 | 01 | T-SOFC403-01 | SOFC403 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC403-02 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | - | [21 empty] | T | SOFC403 | 02 | T-SOFC403-02 | SOFC403 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC403-03 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | - | [21 empty] | T | SOFC403 | 03 | T-SOFC403-03 | SOFC403 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC403-04 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | - | [21 empty] | T | SOFC403 | 04 | T-SOFC403-04 | SOFC403 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC403-05 | C |  | STP-CAT.5e | 4P | 24AWG | 24 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #403 | FUEL CELL #403 | - | [21 empty] | T | SOFC403 | 05 | T-SOFC403-05 | SOFC403 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC404-01 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | X-PA-930 | 16 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | - | [21 empty] | T | SOFC404 | 01 | T-SOFC404-01 | SOFC404 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC404-02 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | - | [21 empty] | T | SOFC404 | 02 | T-SOFC404-02 | SOFC404 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC404-03 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | - | [21 empty] | T | SOFC404 | 03 | T-SOFC404-03 | SOFC404 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC404-04 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | - | [21 empty] | T | SOFC404 | 04 | T-SOFC404-04 | SOFC404 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC404-05 | C |  | STP-CAT.5e | 4P | 24AWG | 31 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #404 | FUEL CELL #404 | - | [21 empty] | T | SOFC404 | 05 | T-SOFC404-05 | SOFC404 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC405-01 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | X-PA-931 | 21 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | - | [21 empty] | T | SOFC405 | 01 | T-SOFC405-01 | SOFC405 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC405-02 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | - | [21 empty] | T | SOFC405 | 02 | T-SOFC405-02 | SOFC405 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC405-03 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | - | [21 empty] | T | SOFC405 | 03 | T-SOFC405-03 | SOFC405 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC405-04 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | - | [21 empty] | T | SOFC405 | 04 | T-SOFC405-04 | SOFC405 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC405-05 | C |  | STP-CAT.5e | 4P | 24AWG | 38 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #405 | FUEL CELL #405 | - | [21 empty] | T | SOFC405 | 05 | T-SOFC405-05 | SOFC405 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC406-01 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | X-PA-932 | 23 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | - | [21 empty] | T | SOFC406 | 01 | T-SOFC406-01 | SOFC406 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC406-02 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | - | [21 empty] | T | SOFC406 | 02 | T-SOFC406-02 | SOFC406 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC406-03 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | - | [21 empty] | T | SOFC406 | 03 | T-SOFC406-03 | SOFC406 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC406-04 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | - | [21 empty] | T | SOFC406 | 04 | T-SOFC406-04 | SOFC406 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC406-05 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #406 | FUEL CELL #406 | - | [21 empty] | T | SOFC406 | 05 | T-SOFC406-05 | SOFC406 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC407-01 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | X-PA-933 | 28 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | - | [21 empty] | T | SOFC407 | 01 | T-SOFC407-01 | SOFC407 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC407-02 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | - | [21 empty] | T | SOFC407 | 02 | T-SOFC407-02 | SOFC407 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC407-03 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | - | [21 empty] | T | SOFC407 | 03 | T-SOFC407-03 | SOFC407 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC407-04 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | - | [21 empty] | T | SOFC407 | 04 | T-SOFC407-04 | SOFC407 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC407-05 | C |  | STP-CAT.5e | 4P | 24AWG | 52 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #407 | FUEL CELL #407 | - | [21 empty] | T | SOFC407 | 05 | T-SOFC407-05 | SOFC407 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC408-01 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | X-PA-934 | 30 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | - | [21 empty] | T | SOFC408 | 01 | T-SOFC408-01 | SOFC408 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC408-02 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | - | [21 empty] | T | SOFC408 | 02 | T-SOFC408-02 | SOFC408 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC408-03 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | - | [21 empty] | T | SOFC408 | 03 | T-SOFC408-03 | SOFC408 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC408-04 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | - | [21 empty] | T | SOFC408 | 04 | T-SOFC408-04 | SOFC408 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC408-05 | C |  | STP-CAT.5e | 4P | 24AWG | 59 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #408 | FUEL CELL #408 | - | [21 empty] | T | SOFC408 | 05 | T-SOFC408-05 | SOFC408 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC409-01 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | X-PA-935 | 34 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | - | [21 empty] | T | SOFC409 | 01 | T-SOFC409-01 | SOFC409 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC409-02 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | - | [21 empty] | T | SOFC409 | 02 | T-SOFC409-02 | SOFC409 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC409-03 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | - | [21 empty] | T | SOFC409 | 03 | T-SOFC409-03 | SOFC409 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC409-04 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | - | [21 empty] | T | SOFC409 | 04 | T-SOFC409-04 | SOFC409 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC409-05 | C |  | STP-CAT.5e | 4P | 24AWG | 66 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #409 | FUEL CELL #409 | - | [21 empty] | T | SOFC409 | 05 | T-SOFC409-05 | SOFC409 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC410-01 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | X-PA-936 | 36 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | - | [21 empty] | T | SOFC410 | 01 | T-SOFC410-01 | SOFC410 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC410-02 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | - | [21 empty] | T | SOFC410 | 02 | T-SOFC410-02 | SOFC410 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC410-03 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | - | [21 empty] | T | SOFC410 | 03 | T-SOFC410-03 | SOFC410 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC410-04 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | - | [21 empty] | T | SOFC410 | 04 | T-SOFC410-04 | SOFC410 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC410-05 | C |  | STP-CAT.5e | 4P | 24AWG | 73 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | SOFC #410 | FUEL CELL #410 | - | [21 empty] | T | SOFC410 | 05 | T-SOFC410-05 | SOFC410 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM401-01 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | X-PA-937 | 8 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | WDM #401 | WATER DISTRIBUTION MODULE #401 | - | [21 empty] | T | WDM401 | 01 | T-WDM401-01 | WDM401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM401-02 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | WDM #401 | WATER DISTRIBUTION MODULE #401 | - | [21 empty] | T | WDM401 | 02 | T-WDM401-02 | WDM401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM401-03 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | WDM #401 | WATER DISTRIBUTION MODULE #401 | - | [21 empty] | T | WDM401 | 03 | T-WDM401-03 | WDM401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM402-01 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | X-PA-938 | 6 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | WDM #402 | WATER DISTRIBUTION MODULE #402 | - | [21 empty] | T | WDM402 | 01 | T-WDM402-01 | WDM402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM402-02 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | WDM #402 | WATER DISTRIBUTION MODULE #402 | - | [21 empty] | T | WDM402 | 02 | T-WDM402-02 | WDM402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM402-03 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | WDM #402 | WATER DISTRIBUTION MODULE #402 | - | [21 empty] | T | WDM402 | 03 | T-WDM402-03 | WDM402 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC501-01 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | X-PA-936 | 8 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | - | [21 empty] | T | SOFC501 | 01 | T-SOFC501-01 | SOFC501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC501-02 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | - | [21 empty] | T | SOFC501 | 02 | T-SOFC501-02 | SOFC501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC501-03 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | - | [21 empty] | T | SOFC501 | 03 | T-SOFC501-03 | SOFC501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC501-04 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | - | [21 empty] | T | SOFC501 | 04 | T-SOFC501-04 | SOFC501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC501-05 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #501 | FUEL CELL #501 | - | [21 empty] | T | SOFC501 | 05 | T-SOFC501-05 | SOFC501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC502-01 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | X-PA-937 | 12 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | - | [21 empty] | T | SOFC502 | 01 | T-SOFC502-01 | SOFC502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC502-02 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | - | [21 empty] | T | SOFC502 | 02 | T-SOFC502-02 | SOFC502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC502-03 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | - | [21 empty] | T | SOFC502 | 03 | T-SOFC502-03 | SOFC502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC502-04 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | - | [21 empty] | T | SOFC502 | 04 | T-SOFC502-04 | SOFC502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC502-05 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #502 | FUEL CELL #502 | - | [21 empty] | T | SOFC502 | 05 | T-SOFC502-05 | SOFC502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC503-01 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | X-PA-938 | 14 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | - | [21 empty] | T | SOFC503 | 01 | T-SOFC503-01 | SOFC503 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC503-02 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | - | [21 empty] | T | SOFC503 | 02 | T-SOFC503-02 | SOFC503 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC503-03 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | - | [21 empty] | T | SOFC503 | 03 | T-SOFC503-03 | SOFC503 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC503-04 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | - | [21 empty] | T | SOFC503 | 04 | T-SOFC503-04 | SOFC503 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC503-05 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #503 | FUEL CELL #503 | - | [21 empty] | T | SOFC503 | 05 | T-SOFC503-05 | SOFC503 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC504-01 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | X-PA-939 | 19 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | - | [21 empty] | T | SOFC504 | 01 | T-SOFC504-01 | SOFC504 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC504-02 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | - | [21 empty] | T | SOFC504 | 02 | T-SOFC504-02 | SOFC504 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC504-03 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | - | [21 empty] | T | SOFC504 | 03 | T-SOFC504-03 | SOFC504 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC504-04 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | - | [21 empty] | T | SOFC504 | 04 | T-SOFC504-04 | SOFC504 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC504-05 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #504 | FUEL CELL #504 | - | [21 empty] | T | SOFC504 | 05 | T-SOFC504-05 | SOFC504 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC505-01 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | X-PA-940 | 21 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | - | [21 empty] | T | SOFC505 | 01 | T-SOFC505-01 | SOFC505 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC505-02 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | - | [21 empty] | T | SOFC505 | 02 | T-SOFC505-02 | SOFC505 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC505-03 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | - | [21 empty] | T | SOFC505 | 03 | T-SOFC505-03 | SOFC505 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC505-04 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | - | [21 empty] | T | SOFC505 | 04 | T-SOFC505-04 | SOFC505 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC505-05 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #505 | FUEL CELL #505 | - | [21 empty] | T | SOFC505 | 05 | T-SOFC505-05 | SOFC505 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC506-01 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | X-PA-941 | 26 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | - | [21 empty] | T | SOFC506 | 01 | T-SOFC506-01 | SOFC506 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC506-02 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | - | [21 empty] | T | SOFC506 | 02 | T-SOFC506-02 | SOFC506 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC506-03 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | - | [21 empty] | T | SOFC506 | 03 | T-SOFC506-03 | SOFC506 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC506-04 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | - | [21 empty] | T | SOFC506 | 04 | T-SOFC506-04 | SOFC506 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC506-05 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #506 | FUEL CELL #506 | - | [21 empty] | T | SOFC506 | 05 | T-SOFC506-05 | SOFC506 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC507-01 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | X-PA-942 | 28 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | - | [21 empty] | T | SOFC507 | 01 | T-SOFC507-01 | SOFC507 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC507-02 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | - | [21 empty] | T | SOFC507 | 02 | T-SOFC507-02 | SOFC507 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC507-03 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | - | [21 empty] | T | SOFC507 | 03 | T-SOFC507-03 | SOFC507 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC507-04 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | - | [21 empty] | T | SOFC507 | 04 | T-SOFC507-04 | SOFC507 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC507-05 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #507 | FUEL CELL #507 | - | [21 empty] | T | SOFC507 | 05 | T-SOFC507-05 | SOFC507 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC508-01 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | X-PA-943 | 32 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | - | [21 empty] | T | SOFC508 | 01 | T-SOFC508-01 | SOFC508 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC508-02 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | - | [21 empty] | T | SOFC508 | 02 | T-SOFC508-02 | SOFC508 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC508-03 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | - | [21 empty] | T | SOFC508 | 03 | T-SOFC508-03 | SOFC508 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC508-04 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | - | [21 empty] | T | SOFC508 | 04 | T-SOFC508-04 | SOFC508 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC508-05 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #508 | FUEL CELL #508 | - | [21 empty] | T | SOFC508 | 05 | T-SOFC508-05 | SOFC508 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC509-01 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | X-PA-944 | 34 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | - | [21 empty] | T | SOFC509 | 01 | T-SOFC509-01 | SOFC509 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC509-02 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | - | [21 empty] | T | SOFC509 | 02 | T-SOFC509-02 | SOFC509 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC509-03 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | - | [21 empty] | T | SOFC509 | 03 | T-SOFC509-03 | SOFC509 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC509-04 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | - | [21 empty] | T | SOFC509 | 04 | T-SOFC509-04 | SOFC509 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC509-05 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | SOFC #509 | FUEL CELL #509 | - | [21 empty] | T | SOFC509 | 05 | T-SOFC509-05 | SOFC509 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM501-01 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | X-PA-945 | 8 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | WDM #501 | WATER DISTRIBUTION MODULE #501 | - | [21 empty] | T | WDM501 | 01 | T-WDM501-01 | WDM501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM501-02 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | WDM #501 | WATER DISTRIBUTION MODULE #501 | - | [21 empty] | T | WDM501 | 02 | T-WDM501-02 | WDM501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM501-03 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | WDM #501 | WATER DISTRIBUTION MODULE #501 | - | [21 empty] | T | WDM501 | 03 | T-WDM501-03 | WDM501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM502-01 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | X-PA-946 | 6 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | WDM #502 | WATER DISTRIBUTION MODULE #502 | - | [21 empty] | T | WDM502 | 01 | T-WDM502-01 | WDM502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM502-02 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | WDM #502 | WATER DISTRIBUTION MODULE #502 | - | [21 empty] | T | WDM502 | 02 | T-WDM502-02 | WDM502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM502-03 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #501 | TELE CABINET #501 | FUEL CELL AREA | WDM #502 | WATER DISTRIBUTION MODULE #502 | - | [21 empty] | T | WDM502 | 03 | T-WDM502-03 | WDM502 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC601-01 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | X-PA-947 | 8 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #601 | FUEL CELL #601 | - | [21 empty] | T | SOFC601 | 01 | T-SOFC601-01 | SOFC601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC601-02 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #601 | FUEL CELL #601 | - | [21 empty] | T | SOFC601 | 02 | T-SOFC601-02 | SOFC601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC601-03 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #601 | FUEL CELL #601 | - | [21 empty] | T | SOFC601 | 03 | T-SOFC601-03 | SOFC601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC601-04 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #601 | FUEL CELL #601 | - | [21 empty] | T | SOFC601 | 04 | T-SOFC601-04 | SOFC601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC601-05 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #601 | FUEL CELL #601 | - | [21 empty] | T | SOFC601 | 05 | T-SOFC601-05 | SOFC601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC602-01 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | X-PA-948 | 12 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | - | [21 empty] | T | SOFC602 | 01 | T-SOFC602-01 | SOFC602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC602-02 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | - | [21 empty] | T | SOFC602 | 02 | T-SOFC602-02 | SOFC602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC602-03 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | - | [21 empty] | T | SOFC602 | 03 | T-SOFC602-03 | SOFC602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC602-04 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | - | [21 empty] | T | SOFC602 | 04 | T-SOFC602-04 | SOFC602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC602-05 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #602 | FUEL CELL #602 | - | [21 empty] | T | SOFC602 | 05 | T-SOFC602-05 | SOFC602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC603-01 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | X-PA-949 | 14 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #603 | FUEL CELL #603 | - | [21 empty] | T | SOFC603 | 01 | T-SOFC603-01 | SOFC603 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC603-02 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #603 | FUEL CELL #603 | - | [21 empty] | T | SOFC603 | 02 | T-SOFC603-02 | SOFC603 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC603-03 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #603 | FUEL CELL #603 | - | [21 empty] | T | SOFC603 | 03 | T-SOFC603-03 | SOFC603 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC603-04 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #603 | FUEL CELL #603 | - | [21 empty] | T | SOFC603 | 04 | T-SOFC603-04 | SOFC603 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC603-05 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #603 | FUEL CELL #603 | - | [21 empty] | T | SOFC603 | 05 | T-SOFC603-05 | SOFC603 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC604-01 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | X-PA-950 | 19 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #604 | FUEL CELL #604 | - | [21 empty] | T | SOFC604 | 01 | T-SOFC604-01 | SOFC604 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC604-02 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #604 | FUEL CELL #604 | - | [21 empty] | T | SOFC604 | 02 | T-SOFC604-02 | SOFC604 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC604-03 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #604 | FUEL CELL #604 | - | [21 empty] | T | SOFC604 | 03 | T-SOFC604-03 | SOFC604 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC604-04 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #604 | FUEL CELL #604 | - | [21 empty] | T | SOFC604 | 04 | T-SOFC604-04 | SOFC604 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC604-05 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #604 | FUEL CELL #604 | - | [21 empty] | T | SOFC604 | 05 | T-SOFC604-05 | SOFC604 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC605-01 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | X-PA-951 | 21 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | - | [21 empty] | T | SOFC605 | 01 | T-SOFC605-01 | SOFC605 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC605-02 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | - | [21 empty] | T | SOFC605 | 02 | T-SOFC605-02 | SOFC605 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC605-03 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | - | [21 empty] | T | SOFC605 | 03 | T-SOFC605-03 | SOFC605 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC605-04 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | - | [21 empty] | T | SOFC605 | 04 | T-SOFC605-04 | SOFC605 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC605-05 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #605 | FUEL CELL #605 | - | [21 empty] | T | SOFC605 | 05 | T-SOFC605-05 | SOFC605 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC606-01 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | X-PA-952 | 26 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | - | [21 empty] | T | SOFC606 | 01 | T-SOFC606-01 | SOFC606 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC606-02 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | - | [21 empty] | T | SOFC606 | 02 | T-SOFC606-02 | SOFC606 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC606-03 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | - | [21 empty] | T | SOFC606 | 03 | T-SOFC606-03 | SOFC606 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC606-04 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | - | [21 empty] | T | SOFC606 | 04 | T-SOFC606-04 | SOFC606 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC606-05 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #606 | FUEL CELL #606 | - | [21 empty] | T | SOFC606 | 05 | T-SOFC606-05 | SOFC606 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC607-01 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | X-PA-953 | 28 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #607 | FUEL CELL #607 | - | [21 empty] | T | SOFC607 | 01 | T-SOFC607-01 | SOFC607 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC607-02 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #607 | FUEL CELL #607 | - | [21 empty] | T | SOFC607 | 02 | T-SOFC607-02 | SOFC607 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC607-03 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #607 | FUEL CELL #607 | - | [21 empty] | T | SOFC607 | 03 | T-SOFC607-03 | SOFC607 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC607-04 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #607 | FUEL CELL #607 | - | [21 empty] | T | SOFC607 | 04 | T-SOFC607-04 | SOFC607 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC607-05 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #607 | FUEL CELL #607 | - | [21 empty] | T | SOFC607 | 05 | T-SOFC607-05 | SOFC607 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC608-01 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | X-PA-954 | 32 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #608 | FUEL CELL #608 | - | [21 empty] | T | SOFC608 | 01 | T-SOFC608-01 | SOFC608 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC608-02 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #608 | FUEL CELL #608 | - | [21 empty] | T | SOFC608 | 02 | T-SOFC608-02 | SOFC608 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC608-03 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #608 | FUEL CELL #608 | - | [21 empty] | T | SOFC608 | 03 | T-SOFC608-03 | SOFC608 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC608-04 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #608 | FUEL CELL #608 | - | [21 empty] | T | SOFC608 | 04 | T-SOFC608-04 | SOFC608 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC608-05 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #608 | FUEL CELL #608 | - | [21 empty] | T | SOFC608 | 05 | T-SOFC608-05 | SOFC608 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC609-01 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | X-PA-955 | 34 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #609 | FUEL CELL #609 | - | [21 empty] | T | SOFC609 | 01 | T-SOFC609-01 | SOFC609 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC609-02 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #609 | FUEL CELL #609 | - | [21 empty] | T | SOFC609 | 02 | T-SOFC609-02 | SOFC609 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC609-03 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #609 | FUEL CELL #609 | - | [21 empty] | T | SOFC609 | 03 | T-SOFC609-03 | SOFC609 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC609-04 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #609 | FUEL CELL #609 | - | [21 empty] | T | SOFC609 | 04 | T-SOFC609-04 | SOFC609 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC609-05 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | SOFC #609 | FUEL CELL #609 | - | [21 empty] | T | SOFC609 | 05 | T-SOFC609-05 | SOFC609 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM601-01 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | X-PA-956 | 8 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | WDM #601 | WATER DISTRIBUTION MODULE #601 | - | [21 empty] | T | WDM601 | 01 | T-WDM601-01 | WDM601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM601-02 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | WDM #601 | WATER DISTRIBUTION MODULE #601 | - | [21 empty] | T | WDM601 | 02 | T-WDM601-02 | WDM601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM601-03 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | WDM #601 | WATER DISTRIBUTION MODULE #601 | - | [21 empty] | T | WDM601 | 03 | T-WDM601-03 | WDM601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM602-01 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | X-PA-957 | 6 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | WDM #602 | WATER DISTRIBUTION MODULE #602 | - | [21 empty] | T | WDM602 | 01 | T-WDM602-01 | WDM602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM602-02 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | WDM #602 | WATER DISTRIBUTION MODULE #602 | - | [21 empty] | T | WDM602 | 02 | T-WDM602-02 | WDM602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM602-03 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | WDM #602 | WATER DISTRIBUTION MODULE #602 | - | [21 empty] | T | WDM602 | 03 | T-WDM602-03 | WDM602 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC701-01 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | X-PA-958 | 8 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | - | [21 empty] | T | SOFC701 | 01 | T-SOFC701-01 | SOFC701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC701-02 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | - | [21 empty] | T | SOFC701 | 02 | T-SOFC701-02 | SOFC701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC701-03 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | - | [21 empty] | T | SOFC701 | 03 | T-SOFC701-03 | SOFC701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC701-04 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | - | [21 empty] | T | SOFC701 | 04 | T-SOFC701-04 | SOFC701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC701-05 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #701 | FUEL CELL #701 | - | [21 empty] | T | SOFC701 | 05 | T-SOFC701-05 | SOFC701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC702-01 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | X-PA-959 | 12 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | - | [21 empty] | T | SOFC702 | 01 | T-SOFC702-01 | SOFC702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC702-02 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | - | [21 empty] | T | SOFC702 | 02 | T-SOFC702-02 | SOFC702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC702-03 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | - | [21 empty] | T | SOFC702 | 03 | T-SOFC702-03 | SOFC702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC702-04 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | - | [21 empty] | T | SOFC702 | 04 | T-SOFC702-04 | SOFC702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC702-05 | C |  | STP-CAT.5e | 4P | 24AWG | 23 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #702 | FUEL CELL #702 | - | [21 empty] | T | SOFC702 | 05 | T-SOFC702-05 | SOFC702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC703-01 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | X-PA-960 | 14 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | - | [21 empty] | T | SOFC703 | 01 | T-SOFC703-01 | SOFC703 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC703-02 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | - | [21 empty] | T | SOFC703 | 02 | T-SOFC703-02 | SOFC703 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC703-03 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | - | [21 empty] | T | SOFC703 | 03 | T-SOFC703-03 | SOFC703 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC703-04 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | - | [21 empty] | T | SOFC703 | 04 | T-SOFC703-04 | SOFC703 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC703-05 | C |  | STP-CAT.5e | 4P | 24AWG | 30 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #703 | FUEL CELL #703 | - | [21 empty] | T | SOFC703 | 05 | T-SOFC703-05 | SOFC703 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC704-01 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | X-PA-961 | 19 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | - | [21 empty] | T | SOFC704 | 01 | T-SOFC704-01 | SOFC704 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC704-02 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | - | [21 empty] | T | SOFC704 | 02 | T-SOFC704-02 | SOFC704 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC704-03 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | - | [21 empty] | T | SOFC704 | 03 | T-SOFC704-03 | SOFC704 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC704-04 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | - | [21 empty] | T | SOFC704 | 04 | T-SOFC704-04 | SOFC704 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC704-05 | C |  | STP-CAT.5e | 4P | 24AWG | 37 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #704 | FUEL CELL #704 | - | [21 empty] | T | SOFC704 | 05 | T-SOFC704-05 | SOFC704 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC705-01 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | X-PA-962 | 21 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | - | [21 empty] | T | SOFC705 | 01 | T-SOFC705-01 | SOFC705 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC705-02 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | - | [21 empty] | T | SOFC705 | 02 | T-SOFC705-02 | SOFC705 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC705-03 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | - | [21 empty] | T | SOFC705 | 03 | T-SOFC705-03 | SOFC705 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC705-04 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | - | [21 empty] | T | SOFC705 | 04 | T-SOFC705-04 | SOFC705 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC705-05 | C |  | STP-CAT.5e | 4P | 24AWG | 44 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #705 | FUEL CELL #705 | - | [21 empty] | T | SOFC705 | 05 | T-SOFC705-05 | SOFC705 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC706-01 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | X-PA-963 | 26 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | - | [21 empty] | T | SOFC706 | 01 | T-SOFC706-01 | SOFC706 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC706-02 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | - | [21 empty] | T | SOFC706 | 02 | T-SOFC706-02 | SOFC706 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC706-03 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | - | [21 empty] | T | SOFC706 | 03 | T-SOFC706-03 | SOFC706 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC706-04 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | - | [21 empty] | T | SOFC706 | 04 | T-SOFC706-04 | SOFC706 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC706-05 | C |  | STP-CAT.5e | 4P | 24AWG | 51 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #706 | FUEL CELL #706 | - | [21 empty] | T | SOFC706 | 05 | T-SOFC706-05 | SOFC706 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC707-01 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | X-PA-964 | 28 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | - | [21 empty] | T | SOFC707 | 01 | T-SOFC707-01 | SOFC707 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC707-02 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | - | [21 empty] | T | SOFC707 | 02 | T-SOFC707-02 | SOFC707 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC707-03 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | - | [21 empty] | T | SOFC707 | 03 | T-SOFC707-03 | SOFC707 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC707-04 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | - | [21 empty] | T | SOFC707 | 04 | T-SOFC707-04 | SOFC707 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC707-05 | C |  | STP-CAT.5e | 4P | 24AWG | 58 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #707 | FUEL CELL #707 | - | [21 empty] | T | SOFC707 | 05 | T-SOFC707-05 | SOFC707 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC708-01 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | X-PA-965 | 32 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | - | [21 empty] | T | SOFC708 | 01 | T-SOFC708-01 | SOFC708 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC708-02 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | - | [21 empty] | T | SOFC708 | 02 | T-SOFC708-02 | SOFC708 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC708-03 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | - | [21 empty] | T | SOFC708 | 03 | T-SOFC708-03 | SOFC708 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC708-04 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | - | [21 empty] | T | SOFC708 | 04 | T-SOFC708-04 | SOFC708 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC708-05 | C |  | STP-CAT.5e | 4P | 24AWG | 65 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #708 | FUEL CELL #708 | - | [21 empty] | T | SOFC708 | 05 | T-SOFC708-05 | SOFC708 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC709-01 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | X-PA-966 | 34 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | - | [21 empty] | T | SOFC709 | 01 | T-SOFC709-01 | SOFC709 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC709-02 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | - | [21 empty] | T | SOFC709 | 02 | T-SOFC709-02 | SOFC709 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC709-03 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | - | [21 empty] | T | SOFC709 | 03 | T-SOFC709-03 | SOFC709 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC709-04 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | - | [21 empty] | T | SOFC709 | 04 | T-SOFC709-04 | SOFC709 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-SOFC709-05 | C |  | STP-CAT.5e | 4P | 24AWG | 72 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | SOFC #709 | FUEL CELL #709 | - | [21 empty] | T | SOFC709 | 05 | T-SOFC709-05 | SOFC709 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM701-01 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | X-PA-967 | 8 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | WDM #701 | WATER DISTRIBUTION MODULE #701 | - | [21 empty] | T | WDM701 | 01 | T-WDM701-01 | WDM701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM701-02 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | WDM #701 | WATER DISTRIBUTION MODULE #701 | - | [21 empty] | T | WDM701 | 02 | T-WDM701-02 | WDM701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM701-03 | C |  | STP-CAT.5e | 4P | 24AWG | 11 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | WDM #701 | WATER DISTRIBUTION MODULE #701 | - | [21 empty] | T | WDM701 | 03 | T-WDM701-03 | WDM701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM702-01 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | X-PA-968 | 6 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | WDM #702 | WATER DISTRIBUTION MODULE #702 | - | [21 empty] | T | WDM702 | 01 | T-WDM702-01 | WDM702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM702-02 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | WDM #702 | WATER DISTRIBUTION MODULE #702 | - | [21 empty] | T | WDM702 | 02 | T-WDM702-02 | WDM702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-WDM702-03 | C |  | STP-CAT.5e | 4P | 24AWG | 9 | 6.5 | 33.19 | [5 empty] | FUEL CELL AREA | TC #701 | TELE CABINET #701 | FUEL CELL AREA | WDM #702 | WATER DISTRIBUTION MODULE #702 | - | [21 empty] | T | WDM702 | 03 | T-WDM702-03 | WDM702 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X
X | #REF! | T-TC101-01 | C |  | STP-CAT.5e | 4P | 24AWG | 82 | 6.5 | 33.19 | X-PA-401 | 15 |  |  |  | 전자기기실 | EL-MDF-001 | MDF & CCTV PANEL | FUEL CELL AREA | TC #101 | TELE CABINET #101 | X-TN-153 X-TN-152 X-TN-151 X-TN-142 X-TN-141 X-TN-140 X-TN-135 X-TL-123 X-TL-116 X-TL-107 X-TL-101 | X-TN-153 | X-TN-152 | X-TN-151 | X-TN-142 | X-TN-141 | X-TN-140 | X-TN-135 | X-TL-123 | X-TL-116 | X-TL-107 | X-TL-101 | [10 empty] | T | TC101 | 01 | T-TC101-01 | TC101 | STP-CAT.5e 4P-24AWG㎟-C
X | #REF! | T-TC201-01 | C |  | STP-CAT.5e | 4P | 24AWG | 16 | 6.5 | 33.19 | X-PA-451 | 15 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | TC #201 | TELE CABINET #201 | - | [21 empty] | T | TC201 | 01 | T-TC201-01 | TC201 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-TC401-01 | C |  | STP-CAT.5e | 4P | 24AWG | 45 | 6.5 | 33.19 | X-PA-683 | 7 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | TC #401 | TELE CABINET #401 | - | [21 empty] | T | TC401 | 01 | T-TC401-01 | TC401 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-TC601-01 | C |  | STP-CAT.5e | 4P | 24AWG | 70 | 6.5 | 33.19 | X-PA-692 | 33 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | FUEL CELL AREA | TC #601 | TELE CABINET #601 | - | [21 empty] | T | TC601 | 01 | T-TC601-01 | TC601 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-TC301-01 | C |  | STP-CAT.5e | 4P | 24AWG | 25 | 6.5 | 33.19 | X-PA-452 | 22 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | FUEL CELL AREA | TC #301 | TELE CABINET #301 | - | [21 empty] | T | TC301 | 01 | T-TC301-01 | TC301 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-TC501-01 | C |  | STP-CAT.5e | 4P | 24AWG | 25 | 6.5 | 33.19 | X-PA-621 | 24 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | FUEL CELL AREA | TC #501 | TELE CABINET #501 | - | [21 empty] | T | TC501 | 01 | T-TC501-01 | TC501 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X | #REF! | T-TC701-01 | C |  | STP-CAT.5e | 4P | 24AWG | 25 | 6.5 | 33.19 | X-PA-622 | 23 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | FUEL CELL AREA | TC #701 | TELE CABINET #701 | - | [21 empty] | T | TC701 | 01 | T-TC701-01 | TC701 | STP-CAT.5e 4P-24AWG㎟-C | bar: L-TD-140 L-TD-140
X
X | #REF! | T-ELLV802-01 | C | 0.6/1kV | FR-3 | 2C | 2.5 | 55 | 12 | 113.1 | - | - |  |  |  | 전자기기실 | FF-FA-001 | 소방수신반 | 전기실 | EL-LV-802 | 380-220V DISTRIBUTION BOARD | X-TL-154 X-TN-153 X-TN-152 X-TN-151 X-TN-142 X-TL-138 X-TL-128 X-TL-129 | X-TL-154 | X-TN-153 | X-TN-152 | X-TN-151 | X-TN-142 | X-TL-138 | X-TL-128 | X-TL-129 | [11 empty] | FIRE ALARM TRIP |  | T | ELLV802 | 01 | T-ELLV802-01 | ELLV802 | 0.6/1kV FR-3 2C-2.5㎟-C
X | #REF! | T-ELLV902-01 | C | 0.6/1kV | FR-3 | 2C | 2.5 | 50 | 12 | 113.1 | - | - |  |  |  | 전자기기실 | FF-FA-001 | 소방수신반 | 전기실 | EL-LV-902 | 380-220V DISTRIBUTION BOARD | X-TL-154 X-TN-153 X-TN-152 X-TN-151 X-TN-142 X-TL-138 X-TL-130 | X-TL-154 | X-TN-153 | X-TN-152 | X-TN-151 | X-TN-142 | X-TL-138 | X-TL-130 | [12 empty] | FIRE ALARM TRIP |  | T | ELLV902 | 01 | T-ELLV902-01 | ELLV902 | 0.6/1kV FR-3 2C-2.5㎟-C
X
X | #REF! | Instrument cable
X | #REF! | K-FC1FQIT101-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 59 | 12 | 113.1 | X-PA-801 | 8 |  |  |  | 전기실 북쪽 | FC1-FQIT-101 |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | K | FC1FQIT101 | 01 | K-FC1FQIT101-01 | INPLC001 | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | T-FC1FQIT101-02 | S | - | UL2919(RS485) | 2P | 24AWG | 59 | 9 | 63.62 | X-PA-802 | 8 |  |  |  | 전기실 북쪽 | FC1-FQIT-101 |  | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | T | FC1FQIT101 | 02 | T-FC1FQIT101-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | K-MEPP001-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 55 | 12 | 113.1 | X-PA-803 | 7 |  |  |  | 전기실 북쪽 | ME-PP-001A/B LCP (FC1-PIT-102) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | K | MEPP001 | 01 | K-MEPP001-01 | INPLC001 | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-MEPP001-02 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 55 | 12 | 113.1 | [5 empty] | 전기실 북쪽 | ME-PP-001A/B LCP (FC1-PIT-104) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | K | MEPP001 | 02 | K-MEPP001-02 | INPLC001 | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | C-MEPP001-01 | C | 0.6/1kV | FR-CVV-S | 10C | 2.5 | 55 | 20.5 | 330.07 | X-PA-804 | 7 |  |  |  | 전기실 북쪽 | ME-PP-001A/B LCP |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | C | MEPP001 | 01 | C-MEPP001-01 | INPLC001 | 0.6/1kV FR-CVV-S 10C-2.5㎟-C
X | #REF! | K-MEGO001SJB-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 6P | 1.5 | 60 | 21.5 | 363.06 | X-PB-805 | 10 |  |  |  | 전기실 북쪽 | NG GOV. SIGNAL J/B |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | K | MEGO001SJB | 01 | K-MEGO001SJB-01 | INPLC001 | 0.6/1kV FR-CVV-I/C AMS 6P-1.5㎟-S
X | #REF! | T-FC1FQIT201-01 | S | - | UL2919(RS485) | 2P | 24AWG | 60 | 9 | 63.62 | X-PB-806 | 10 |  |  |  | 전기실 북쪽 | NG GOV. SIGNAL J/B (FC1-FQIT-201) |  | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | T | FC1FQIT201 | 01 | T-FC1FQIT201-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | K-FC1FQIT201-02 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 60 | 12 | 113.1 | [5 empty] | 전기실 북쪽 | NG GOV. SIGNAL J/B (FC1-FQIT-201) |  | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [11 empty] | (DC 24V, BARRIER) | 190822 | K | FC1FQIT201 | 02 | K-FC1FQIT201-02 | INPLC001 | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | T-FC1FQIT202-01 | S | - | UL2919(RS485) | 2P | 24AWG | 60 | 9 | 63.62 | [5 empty] | 전기실 북쪽 | NG GOV. SIGNAL J/B (FC1-FQIT-202) |  | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [12 empty] | 190822 | T | FC1FQIT202 | 01 | T-FC1FQIT202-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | K-FC1FQIT202-02 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 60 | 12 | 113.1 | [5 empty] | 전기실 북쪽 | NG GOV. SIGNAL J/B (FC1-FQIT-202) |  | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [11 empty] | (DC 24V, BARRIER) | 190822 | K | FC1FQIT202 | 02 | K-FC1FQIT202-02 | INPLC001 | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD201-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 58 | 12.5 | 122.72 | X-PA-807 | 10 |  |  |  | 전기실 북쪽 | NG GOV. SIGNAL J/B (FC1-GD-201) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-115 X-TL-118 X-TL-128 X-TL-138 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-115 | X-TL-118 | X-TL-128 | X-TL-138 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [11 empty] | 190822 | K | FC1GD201 | 01 | K-FC1GD201-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD211-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 75 | 12.5 | 122.72 | X-PA-402 | 10 |  |  |  | FUEL CELL AREA | 2ND GOV. J/B (FC1-GD-211) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (STAMP-1) | 191018 | K | FC1GD211 | 01 | K-FC1GD211-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1PIT217-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 75 | 12 | 113.1 | [5 empty] | FUEL CELL AREA | 2ND GOV. J/B (FC1-PIT-217) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | (STAMP-1) | 191018 | K | FC1PIT217 | 01 | K-FC1PIT217-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD221-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 95 | 12.5 | 122.72 | X-PA-422 | 15 |  |  |  | FUEL CELL AREA | 2ND GOV. J/B (FC1-GD-221) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (STAMP-2) | 191018 | K | FC1GD221 | 01 | K-FC1GD221-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1PIT227-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 95 | 12 | 113.1 | [5 empty] | FUEL CELL AREA | 2ND GOV. J/B (FC1-PIT-227) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | (STAMP-2) | 191018 | K | FC1PIT227 | 01 | K-FC1PIT227-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD231-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 102 | 12.5 | 122.72 | X-PA-423 | 22 |  |  |  | FUEL CELL AREA | 2ND GOV. J/B (FC1-GD-231) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (STAMP-3) | 191018 | K | FC1GD231 | 01 | K-FC1GD231-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1PIT237-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 102 | 12 | 113.1 | [5 empty] | FUEL CELL AREA | 2ND GOV. J/B (FC1-PIT-237) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | (STAMP-3) | 191018 | K | FC1PIT237 | 01 | K-FC1PIT237-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD241-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 125 | 12.5 | 122.72 | X-PA-662 | 11 |  |  |  | FUEL CELL AREA | 2ND GOV. J/B (FC1-GD-241) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (STAMP-4) | 191018 | K | FC1GD241 | 01 | K-FC1GD241-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1PIT247-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 125 | 12 | 113.1 | [5 empty] | FUEL CELL AREA | 2ND GOV. J/B (FC1-PIT-247) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | (STAMP-4) | 191018 | K | FC1PIT247 | 01 | K-FC1PIT247-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD251-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 132 | 12.5 | 122.72 | X-PA-661 | 16 |  |  |  | FUEL CELL AREA | 2ND GOV. J/B (FC1-GD-251) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (STAMP-5) | 191018 | K | FC1GD251 | 01 | K-FC1GD251-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1PIT257-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 132 | 12 | 113.1 | [5 empty] | FUEL CELL AREA | 2ND GOV. J/B (FC1-PIT-257) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | (STAMP-5) | 191018 | K | FC1PIT257 | 01 | K-FC1PIT257-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD261-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 150 | 12.5 | 122.72 | X-PA-682 | 38 |  |  |  | FUEL CELL AREA | 2ND GOV. J/B (FC1-GD-261) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (STAMP-6) | 191018 | K | FC1GD261 | 01 | K-FC1GD261-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1PIT267-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 150 | 12 | 113.1 | [5 empty] | FUEL CELL AREA | 2ND GOV. J/B (FC1-PIT-267) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | (STAMP-6) | 191018 | K | FC1PIT267 | 01 | K-FC1PIT267-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD271-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 157 | 12.5 | 122.72 | X-PA-681 | 45 |  |  |  | FUEL CELL AREA | 2ND GOV. J/B (FC1-GD-271) |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (STAMP-7) | 191018 | K | FC1GD271 | 01 | K-FC1GD271-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1PIT277-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 | 157 | 12 | 113.1 | [5 empty] | FUEL CELL AREA | 2ND GOV. J/B (FC1-PIT-277) |  | 전자기기실 | IN-PLC-002 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [8 empty] | (STAMP-7) | 191018 | K | FC1PIT277 | 01 | K-FC1PIT277-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S
X | #REF! | K-FC1GD301-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 80 | 12.5 | 122.72 | X-PA-002 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-301 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#101) | 190822 | K | FC1GD301 | 01 | K-FC1GD301-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD302-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 80 | 12.5 | 122.72 | X-PA-051 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-302 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#102) | 190822 | K | FC1GD302 | 01 | K-FC1GD302-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD303-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 82 | 12.5 | 122.72 | X-PA-092 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-303 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#103) | 190822 | K | FC1GD303 | 01 | K-FC1GD303-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD304-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 87 | 12.5 | 122.72 | X-PA-131 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-304 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#104) | 190822 | K | FC1GD304 | 01 | K-FC1GD304-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD305-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 89 | 12.5 | 122.72 | X-PA-201 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-305 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#105) | 190822 | K | FC1GD305 | 01 | K-FC1GD305-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD306-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 68 | 12.5 | 122.72 | X-PA-241 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-306 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#106) | 190822 | K | FC1GD306 | 01 | K-FC1GD306-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD307-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 70 | 12.5 | 122.72 | X-PA-281 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-307 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#107) | 190822 | K | FC1GD307 | 01 | K-FC1GD307-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD308-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 74 | 12.5 | 122.72 | X-PA-331 | 13 |  |  |  | FUEL CELL AREA | FC1-GD-308 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#108) | 190822 | K | FC1GD308 | 01 | K-FC1GD308-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD309-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 76 | 12.5 | 122.72 | X-PA-501 | 16 |  |  |  | FUEL CELL AREA | FC1-GD-309 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#109) | 190822 | K | FC1GD309 | 01 | K-FC1GD309-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD310-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 88 | 12.5 | 122.72 | X-PA-411 | 24 |  |  |  | FUEL CELL AREA | FC1-GD-310 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#201) | 190822 | K | FC1GD310 | 01 | K-FC1GD310-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD311-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 86 | 12.5 | 122.72 | X-PA-011 | 21 |  |  |  | FUEL CELL AREA | FC1-GD-311 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#202) | 190822 | K | FC1GD311 | 01 | K-FC1GD311-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD312-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 86 | 12.5 | 122.72 | X-PA-061 | 21 |  |  |  | FUEL CELL AREA | FC1-GD-312 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#203) | 190822 | K | FC1GD312 | 01 | K-FC1GD312-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD313-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 88 | 12.5 | 122.72 | X-PA-091 | 22 |  |  |  | FUEL CELL AREA | FC1-GD-313 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#204) | 190822 | K | FC1GD313 | 01 | K-FC1GD313-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD314-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 93 | 12.5 | 122.72 | X-PA-141 | 21 |  |  |  | FUEL CELL AREA | FC1-GD-314 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#205) | 190822 | K | FC1GD314 | 01 | K-FC1GD314-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD315-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 95 | 12.5 | 122.72 | X-PA-212 | 21 |  |  |  | FUEL CELL AREA | FC1-GD-315 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#206) | 190822 | K | FC1GD315 | 01 | K-FC1GD315-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD316-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 74 | 12.5 | 122.72 | X-PA-251 | 21 |  |  |  | FUEL CELL AREA | FC1-GD-316 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#207) | 190822 | K | FC1GD316 | 01 | K-FC1GD316-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD317-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 76 | 12.5 | 122.72 | X-PA-291 | 21 |  |  |  | FUEL CELL AREA | FC1-GD-317 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#208) | 190822 | K | FC1GD317 | 01 | K-FC1GD317-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD318-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 80 | 12.5 | 122.72 | X-PA-341 | 21 |  |  |  | FUEL CELL AREA | FC1-GD-318 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#209) | 190822 | K | FC1GD318 | 01 | K-FC1GD318-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD319-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 82 | 12.5 | 122.72 | X-PA-511 | 26 |  |  |  | FUEL CELL AREA | FC1-GD-319 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#210) | 190822 | K | FC1GD319 | 01 | K-FC1GD319-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD320-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 108 | 12.5 | 122.72 | X-PA-431 | 41 |  |  |  | FUEL CELL AREA | FC1-GD-320 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#301) | 190822 | K | FC1GD320 | 01 | K-FC1GD320-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD321-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 106 | 12.5 | 122.72 | X-PA-001 | 38 |  |  |  | FUEL CELL AREA | FC1-GD-321 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#302) | 190822 | K | FC1GD321 | 01 | K-FC1GD321-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD322-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 106 | 12.5 | 122.72 | X-PA-062 | 38 |  |  |  | FUEL CELL AREA | FC1-GD-322 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#303) | 190822 | K | FC1GD322 | 01 | K-FC1GD322-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD323-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 108 | 12.5 | 122.72 | X-PA-102 | 38 |  |  |  | FUEL CELL AREA | FC1-GD-323 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#304) | 190822 | K | FC1GD323 | 01 | K-FC1GD323-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD324-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 113 | 12.5 | 122.72 | X-PA-151 | 38 |  |  |  | FUEL CELL AREA | FC1-GD-324 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#305) | 190822 | K | FC1GD324 | 01 | K-FC1GD324-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD325-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 115 | 12.5 | 122.72 | X-PA-211 | 38 |  |  |  | FUEL CELL AREA | FC1-GD-325 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#306) | 190822 | K | FC1GD325 | 01 | K-FC1GD325-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD326-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 94 | 12.5 | 122.72 | X-PA-252 | 38 |  |  |  | FUEL CELL AREA | FC1-GD-326 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#307) | 190822 | K | FC1GD326 | 01 | K-FC1GD326-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD327-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 96 | 12.5 | 122.72 | X-PA-302 | 39 |  |  |  | FUEL CELL AREA | FC1-GD-327 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#308) | 190822 | K | FC1GD327 | 01 | K-FC1GD327-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD328-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 100 | 12.5 | 122.72 | X-PA-342 | 38 |  |  |  | FUEL CELL AREA | FC1-GD-328 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#309) | 190822 | K | FC1GD328 | 01 | K-FC1GD328-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD329-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 102 | 12.5 | 122.72 | X-PA-512 | 43 |  |  |  | FUEL CELL AREA | FC1-GD-329 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#310) | 190822 | K | FC1GD329 | 01 | K-FC1GD329-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD330-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 116 | 12.5 | 122.72 | X-PA-651 | 48 |  |  |  | FUEL CELL AREA | FC1-GD-330 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#401) | 190822 | K | FC1GD330 | 01 | K-FC1GD330-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD331-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 112 | 12.5 | 122.72 | X-PA-021 | 46 |  |  |  | FUEL CELL AREA | FC1-GD-331 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#402) | 190822 | K | FC1GD331 | 01 | K-FC1GD331-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD332-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 112 | 12.5 | 122.72 | X-PA-071 | 46 |  |  |  | FUEL CELL AREA | FC1-GD-332 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#403) | 190822 | K | FC1GD332 | 01 | K-FC1GD332-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD333-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 114 | 12.5 | 122.72 | X-PA-101 | 46 |  |  |  | FUEL CELL AREA | FC1-GD-333 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#404) | 190822 | K | FC1GD333 | 01 | K-FC1GD333-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD334-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 119 | 12.5 | 122.72 | X-PA-152 | 47 |  |  |  | FUEL CELL AREA | FC1-GD-334 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#405) | 190822 | K | FC1GD334 | 01 | K-FC1GD334-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD335-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 121 | 12.5 | 122.72 | X-PA-222 | 46 |  |  |  | FUEL CELL AREA | FC1-GD-335 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#406) | 190822 | K | FC1GD335 | 01 | K-FC1GD335-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD336-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 100 | 12.5 | 122.72 | X-PA-261 | 46 |  |  |  | FUEL CELL AREA | FC1-GD-336 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#407) | 190822 | K | FC1GD336 | 01 | K-FC1GD336-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD337-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 102 | 12.5 | 122.72 | X-PA-301 | 46 |  |  |  | FUEL CELL AREA | FC1-GD-337 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#408) | 190822 | K | FC1GD337 | 01 | K-FC1GD337-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD338-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 106 | 12.5 | 122.72 | X-PA-351 | 46 |  |  |  | FUEL CELL AREA | FC1-GD-338 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#409) | 190822 | K | FC1GD338 | 01 | K-FC1GD338-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD339-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 108 | 12.5 | 122.72 | X-PA-721 | 49 |  |  |  | FUEL CELL AREA | FC1-GD-339 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#410) | 190822 | K | FC1GD339 | 01 | K-FC1GD339-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD340-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 132 | 12.5 | 122.72 | X-PA-031 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-340 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#501) | 190822 | K | FC1GD340 | 01 | K-FC1GD340-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD341-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 132 | 12.5 | 122.72 | X-PA-072 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-341 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#502) | 190822 | K | FC1GD341 | 01 | K-FC1GD341-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD342-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 134 | 12.5 | 122.72 | X-PA-111 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-342 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#503) | 190822 | K | FC1GD342 | 01 | K-FC1GD342-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD343-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 139 | 12.5 | 122.72 | X-PA-161 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-343 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#504) | 190822 | K | FC1GD343 | 01 | K-FC1GD343-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD344-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 141 | 12.5 | 122.72 | X-PA-221 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-344 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#505) | 190822 | K | FC1GD344 | 01 | K-FC1GD344-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD345-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 120 | 12.5 | 122.72 | X-PA-262 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-345 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#506) | 190822 | K | FC1GD345 | 01 | K-FC1GD345-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD346-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 122 | 12.5 | 122.72 | X-PA-312 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-346 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#507) | 190822 | K | FC1GD346 | 01 | K-FC1GD346-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD347-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 126 | 12.5 | 122.72 | X-PA-352 | 63 |  |  |  | FUEL CELL AREA | FC1-GD-347 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#508) | 190822 | K | FC1GD347 | 01 | K-FC1GD347-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD348-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 128 | 12.5 | 122.72 | X-PA-732 | 66 |  |  |  | FUEL CELL AREA | FC1-GD-348 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#509) | 190822 | K | FC1GD348 | 01 | K-FC1GD348-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD349-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 138 | 12.5 | 122.72 | X-PA-042 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-349 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#601) | 190822 | K | FC1GD349 | 01 | K-FC1GD349-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD350-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 138 | 12.5 | 122.72 | X-PA-081 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-350 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#602) | 190822 | K | FC1GD350 | 01 | K-FC1GD350-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD351-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 140 | 12.5 | 122.72 | X-PA-122 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-351 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#603) | 190822 | K | FC1GD351 | 01 | K-FC1GD351-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD352-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 145 | 12.5 | 122.72 | X-PA-162 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-352 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#604) | 190822 | K | FC1GD352 | 01 | K-FC1GD352-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD353-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 147 | 12.5 | 122.72 | X-PA-232 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-353 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#605) | 190822 | K | FC1GD353 | 01 | K-FC1GD353-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD354-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 126 | 12.5 | 122.72 | X-PA-271 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-354 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#606) | 190822 | K | FC1GD354 | 01 | K-FC1GD354-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD355-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 128 | 12.5 | 122.72 | X-PA-311 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-355 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#607) | 190822 | K | FC1GD355 | 01 | K-FC1GD355-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD356-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 132 | 12.5 | 122.72 | X-PA-361 | 71 |  |  |  | FUEL CELL AREA | FC1-GD-356 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#608) | 190822 | K | FC1GD356 | 01 | K-FC1GD356-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD357-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 134 | 12.5 | 122.72 | X-PA-731 | 75 |  |  |  | FUEL CELL AREA | FC1-GD-357 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#609) | 190822 | K | FC1GD357 | 01 | K-FC1GD357-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD358-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 158 | 12.5 | 122.72 | X-PA-041 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-358 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#701) | 190822 | K | FC1GD358 | 01 | K-FC1GD358-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD359-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 158 | 12.5 | 122.72 | X-PA-082 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-359 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#702) | 190822 | K | FC1GD359 | 01 | K-FC1GD359-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD360-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 160 | 12.5 | 122.72 | X-PA-121 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-360 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#703) | 190822 | K | FC1GD360 | 01 | K-FC1GD360-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD361-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 165 | 12.5 | 122.72 | X-PA-171 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-361 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [7 empty] | (SOFC#704) | 190822 | K | FC1GD361 | 01 | K-FC1GD361-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD362-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 167 | 12.5 | 122.72 | X-PA-231 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-362 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#705) | 190822 | K | FC1GD362 | 01 | K-FC1GD362-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD363-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 146 | 12.5 | 122.72 | X-PA-272 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-363 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#706) | 190822 | K | FC1GD363 | 01 | K-FC1GD363-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD364-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 148 | 12.5 | 122.72 | X-PA-321 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-364 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#707) | 190822 | K | FC1GD364 | 01 | K-FC1GD364-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD365-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 152 | 12.5 | 122.72 | X-PA-362 | 85 |  |  |  | FUEL CELL AREA | FC1-GD-365 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#708) | 190822 | K | FC1GD365 | 01 | K-FC1GD365-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | K-FC1GD366-01 | S | 0.6/1kV | FR-CVV-I/C AMS | 1T | 1.5 | 154 | 12.5 | 122.72 | X-PA-742 | 91 |  |  |  | FUEL CELL AREA | FC1-GD-366 |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | X-TL-131 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 X-TL-154 | X-TL-131 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | X-TL-154 | [10 empty] | (SOFC#709) | 190822 | K | FC1GD366 | 01 | K-FC1GD366-01 | LATER | 0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S
X | #REF! | T-GDRP-01 | S | - | UL2919(RS485) | 2P | 24AWG | 10 | 9 | 63.62 | - | - |  |  |  | 전자기기실 | GDRP | GAS DETECTOR PANEL | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-154 X-TN-153 | L-TD-140 L-TD-140: X-TL-154; L-TD-141 L-TD-141: X-TN-153 | [14 empty] | 190822 | T | GDRP | 01 | T-GDRP-01 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-SIGNBOARD-01 | S | - | UL2919(RS485) | 2P | 24AWG | 35 | 9 | 63.62 | X-PA-811 | 6 |  |  |  | 전자기기실 | IN-PLC-001 | PLC PANEL | 전기실 동쪽 | SIGNBOARD | 옥외현황판 | X-TN-153 X-TN-152 X-TN-151 X-TN-142 X-TL-138 X-TL-128 X-TL-129 | X-TN-153 | X-TN-152 | X-TN-151 | X-TN-142 | X-TL-138 | X-TL-128 | X-TL-129 | [13 empty] | 190822 | T | SIGNBOARD | 01 | T-SIGNBOARD-01 | LATER | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-TC101-02 | S | - | UL2919(RS485) | 2P | 24AWG | 82 | 9 | 63.62 | X-PA-401 | 15 |  |  |  | FUEL CELL AREA | TC #101 | TELE CABINET #101 | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [9 empty] | 190822 | T | TC101 | 02 | T-TC101-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-TC201-02 | S | - | UL2919(RS485) | 2P | 24AWG | 92 | 9 | 63.62 | X-PA-412 | 25 |  |  |  | FUEL CELL AREA | TC #201 | TELE CABINET #201 | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [9 empty] | 190822 | T | TC201 | 02 | T-TC201-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-TC301-02 | S | - | UL2919(RS485) | 2P | 24AWG | 110 | 9 | 63.62 | X-PA-421 | 42 |  |  |  | FUEL CELL AREA | TC #301 | TELE CABINET #301 | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [9 empty] | 190822 | T | TC301 | 02 | T-TC301-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-TC401-02 | S | - | UL2919(RS485) | 2P | 24AWG | 120 | 9 | 63.62 | X-PA-652 | 6 |  |  |  | FUEL CELL AREA | TC #401 | TELE CABINET #401 | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [9 empty] | 190822 | T | TC401 | 02 | T-TC401-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-TC501-02 | S | - | UL2919(RS485) | 2P | 24AWG | 138 | 9 | 63.62 | X-PA-672 | 25 |  |  |  | FUEL CELL AREA | TC #501 | TELE CABINET #501 | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [9 empty] | 190822 | T | TC501 | 02 | T-TC501-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-TC601-02 | S | - | UL2919(RS485) | 2P | 24AWG | 148 | 9 | 63.62 | X-PA-671 | 33 |  |  |  | FUEL CELL AREA | TC #601 | TELE CABINET #601 | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [9 empty] | 190822 | T | TC601 | 02 | T-TC601-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-TC701-02 | S | - | UL2919(RS485) | 2P | 24AWG | 165 | 9 | 63.62 | X-PA-691 | 49 |  |  |  | FUEL CELL AREA | TC #701 | TELE CABINET #701 | 전자기기실 | IN-PLC-001 | PLC PANEL | X-TL-101 X-TL-107 X-TL-116 X-TL-123 X-TN-135 X-TN-140 X-TN-141 X-TN-142 X-TN-151 X-TN-152 X-TN-153 | X-TL-101 | X-TL-107 | X-TL-116 | X-TL-123 | X-TN-135 | X-TN-140 | X-TN-141 | X-TN-142 | X-TN-151 | X-TN-152 | X-TN-153 | [9 empty] | 190822 | T | TC701 | 02 | T-TC701-02 | INPLC001 | - UL2919(RS485) 2P-24AWG㎟-S
X | #REF! | T-INOWS001-01 | S | F.O CABLE | SINGLE MODE | 4C | 0 | 110 | 9.5 | 70.89 | X-PC-751 | 40 |  |  |  | 전자기기실 | IN-PLC-001 | PLC PANEL | 사무동 | IN-OWS-001 | 사무동 주제어실 OWS | X-TN-153 X-TN-152 X-TN-151 X-TN-142 X-TN-141 X-TN-140 X-TN-135 X-TL-131 | X-TN-153 | X-TN-152 | X-TN-151 | X-TN-142 | X-TN-141 | X-TN-140 | X-TN-135 | X-TL-131 | [12 empty] | 190822 | T | INOWS001 | 01 | T-INOWS001-01 | LATER | F.O CABLE SINGLE MODE 4C-0㎟-S
X | #REF! | T-INOWS001-02 | S | F.O CABLE | SINGLE MODE | 4C | 0 | 110 | 9.5 | 70.89 | X-PC-751 | 40 |  |  |  | 전자기기실 | IN-PLC-001 | PLC PANEL | 사무동 | IN-OWS-001 | 사무동 주제어실 OWS | X-TN-153 X-TN-152 X-TN-151 X-TN-142 X-TN-141 X-TN-140 X-TN-135 X-TL-131 | X-TN-153 | X-TN-152 | X-TN-151 | X-TN-142 | X-TN-141 | X-TN-140 | X-TN-135 | X-TL-131 | [12 empty] | 190822 | T | INOWS001 | 02 | T-INOWS001-02 | LATER | F.O CABLE SINGLE MODE 4C-0㎟-S

## Cable 물량 집계 (hidden)
CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 합계 : LENGTH | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 합계 : LENGTH | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 합계 : LENGTH
P | 0.6/1kV | FR-CV | 1C | 185 |  | C | 0.6/1kV | FR-3 | 2C | 2.5 |  | S | - | UL2919(RS485) | 2P | 24AWG
|  |  | 2C | 4 |  |  |  | FR-CVV-S | 10C | 2.5 |  |  | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5
|  |  |  | 6 |  |  |  |  | 3C | 2.5 |  |  |  |  | 1T | 1.5
|  |  |  | 10 |  |  |  |  | 4C | 2.5 |  |  |  |  | 2P | 1.5
|  |  |  | 16 |  |  | (empty) | STP-CAT.5e | 4P | 24AWG |  |  |  |  | 6P | 1.5
|  |  |  | 25 |  | Total Result | [6 empty] | F.O CABLE | SINGLE MODE | 4C | 0
|  |  |  | 35 | [7 empty] | Total Result
|  |  | 3C | 6
25
|  |  | 4C | 6
10
25
| 22.9kV | FR-CN/CO-W | 1C | 100
Total Result

## Terminal Lug 물량 집계 (hidden)
CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m] |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m] |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m] |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m] |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m] |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m] |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m] |  |  | CATEGORY | VOLTAGE [kV] | TYPE | CORE | SIZE [mm2] | 개수 : LENGTH [m]
P | 0.6/1kV | FR-CV | 2C | 35 |  |  |  | C | 0.6/1kV | FR-3 | 2C | 2.5 |  |  |  | P | 0.6/1kV | FR-CV | 2C | 4 |  |  |  | P | 0.6/1kV | FR-CV | 2C | 6 |  |  |  | P | 0.6/1kV | FR-CV | 2C | 10 |  |  |  | P | 0.6/1kV | FR-CV | 2C | 16 |  |  |  | P | 0.6/1kV | FR-CV | 2C | 25 |  |  |  | P | 0.6/1kV | FR-CV | 1C | 185
S | 0.6/1kV | FR-CVV-I/C AMS | 1P | 1.5 |  | 12 | 48 |  |  | FR-CVV-S | 10C | 2.5 |  | 2 | 8 |  |  |  |  | 35 |  | 31 | 124 |  |  |  |  | 35 |  | 66 | 264 |  |  |  |  | 35 |  | 8 | 32 |  |  |  |  | 35 |  | 8 | 32 |  |  |  |  | 35 |  | 8 | 32 |  |  |  | 2C | 35 |  | 396 | 792
|  |  | 1T | 1.5 |  | 74 | 444 |  |  |  | 3C | 2.5 |  | 22 | 440 | Total Result | [6 empty] | 124 |  |  |  | 3C | 6 |  | 2 | 12 |  |  |  | 4C | 10 |  | 13 | 104 | Total Result | [6 empty] | 32 |  |  |  | 3C | 25 |  | 1 | 6 | Total Result | [6 empty] | 792
|  |  | 2P | 1.5 |  | 6 | 48 |  |  |  | 4C | 2.5 |  | 25 | 150 | [11 empty] | 4C | 6 |  |  | 276 | Total Result | [18 empty] | 4C | 25 |  | 2 | 16
|  |  | 6P | 1.5 |  | 1 | 24 | P | 0.6/1kV | FR-CV | 2C | 35 |  | 43 | 344 | [8 empty] | Total Result | [14 empty] | 136 | [8 empty] | Total Result | [6 empty] | 54
Total Result | [6 empty] | 564 | Total Result | [6 empty] | 942

## Conduit & Fitting 물량 집계 (hidden)
HDG 28mm |  | HDG 36mm |  | ELP 30mm |  | ELP 50mm |  | ELP 100mm |  | MATERIAL | 피벗테이블 물량 | OUTDOOR 중 CABLE 같이 사용하는 배관 | CONDUIT NO. or EQ NO. | 전기실 주변 부하용으로 ELP가기 전까지 전기실 내부 HDG 배관 | CONDUIT NO. or EQ NO. | INST. HOOK-UP DWG 표기 물량 |  |  |  |  | TOTAL [m]
CONDUIT NUMBER | 합계 : CONDUIT | CONDUIT NUMBER | 합계 : CONDUIT | CONDUIT NUMBER | 합계 : CONDUIT | CONDUIT NUMBER | 합계 : CONDUIT | CONDUIT NUMBER | 합계 : CONDUIT | [6 empty] | MASS FLOW METER (WATER FLOW METER) | PRESS TRANSMITTER (CITY WATER PUMP LCP) | GAS DETECTOR (FUEL CELL : 66EA) | 1st GOVERNOR | 2nd GOVERNOR (7EA)
K-RB-821 | 8 | K-RC-801 | 16 | K-PA-004 | 10 | K-PB-001 | 13 | K-PC-002 | 13 | HDG 22mm | [7 empty] | 66 |  |  | 66
K-RB-826 | 10 | K-RC-802 | 18 | K-PA-005 | 8 | K-PB-031 | 71 | K-PC-003 | 13 | HDG 28mm | 18 |  |  | 70 | NG GOV, CITY WATER PUMP WATER FLOW METER | 3 | 2 |  | 2 | 7 | 102
Total Result | 18 | K-RC-803 | 20 | K-PA-035 | 10 | K-PB-034 | 63 | K-PC-011 | 38 | HDG 36mm | 233 |  |  | 60 | NG GOV,CITY WATER PUMP, | [5 empty] | 293
|  | K-RC-804 | 22 | K-PA-036 | 8 | K-PB-041 | 85 | K-PC-012 | 38 | HDG 42mm |  |  |  | 60 | NG GOV,CITY WATER PUMP, |  | 3 |  | 2 |  | 65
|  | K-RC-805 | 24 | K-PA-037 | 10 | K-PB-101 | 38 | K-PC-013 | 21 | ELP 30mm | 5713 | 42 | X-PA-521 | [7 empty] | 5755
|  | K-RC-806 | 18 | K-PA-038 | 8 | K-PB-104 | 22 | K-PC-014 | 21 | ELP 50mm | 1687 | 171 | X-PB-432,X-PB-442,X-PB-621, X-PB-513 | [7 empty] | 1858
|  | K-RC-809 | 10 | K-PA-044 | 10 | K-PB-113 | 46 | K-PC-021 | 63 | ELP 100mm | 6438 | 510 | K-PC-431,K-PC-443,SPAREx4, X-PC-531,SPAREx5 | [7 empty] | 6948
|  | K-RC-810 | 16 | K-PA-045 | 8 | K-PB-133 | 13 | K-PC-022 | 63 | FLEX. CONDUIT 22mm (EX) | [7 empty] | 66 |  | 14 | 80 | EA
|  | K-RC-811 | 21 | K-PA-105 | 8 | K-PB-143 | 21 | K-PC-023 | 46 | FLEX. CONDUIT 28mm | [5 empty] | 3 | 2 |  |  |  | 5 | EA
|  | K-RC-812 | 19 | K-PA-106 | 10 | K-PB-151 | 38 | K-PC-024 | 46 | FLEX. CONDUIT 28mm (EX) | [8 empty] | 2 |  | 2 | EA
|  | K-RC-813 | 17 | K-PA-107 | 8 | K-PB-154 | 47 | K-PC-042 | 85 | FLEX. CONDUIT 42mm | [6 empty] | 3 |  |  |  | 3 | EA
|  | K-RC-814 | 17 | K-PA-116 | 8 | K-PB-163 | 63 | K-PC-043 | 85 | FLEX. CONDUIT 42mm (EX) | [8 empty] | 2 |  | 2 | EA
|  | K-RC-815 | 15 | K-PA-117 | 10 | K-PB-164 | 71 | K-PC-051 | 13 | CONNECTOR (ELP30-HDG22) | [7 empty] | 66 |  |  | 66 | EA
|  | Total Result | 233 | K-PA-118 | 8 | K-PB-175 | 85 | K-PC-052 | 13 | CONNECTOR (ELP30-HDG28) | [5 empty] | 3 | 2 |  | 2 | 7 | 14 | EA
|  |  |  | K-PA-125 | 8 | K-PB-281 | 13 | K-PC-061 | 21 | CONNECTOR (ELP50-HDG42) | [6 empty] | 3 |  | 2 |  | 5 | EA
|  |  |  | K-PA-126 | 10 | K-PB-293 | 21 | K-PC-062 | 21 | SEALING FITTING 22mm | [9 empty] | 14 | 14 | EA
|  |  |  | K-PA-127 | 8 | K-PB-301 | 46 | K-PC-063 | 38 | SEALING FITTING 28mm | [8 empty] | 2 | 7 | 9 | EA
|  |  |  | K-PA-134 | 8 | K-PB-304 | 39 | K-PC-064 | 38 | SEALING FITTING 42mm | [8 empty] | 2 |  | 2 | EA
|  |  |  | K-PA-135 | 11 | K-PB-311 | 71 | K-PC-071 | 46 | NIPPLE 22mm | [9 empty] | 14 | 14 | EA
|  |  |  | K-PA-146 | 8 | K-PB-312 | 63 | K-PC-072 | 46 | NIPPLE 28mm | [8 empty] | 2 | 7 | 9 | EA
|  |  |  | K-PA-147 | 11 | K-PB-321 | 85 | K-PC-073 | 63 | NIPPLE 42mm | [8 empty] | 2 |  | 2 | EA
|  |  |  | K-PA-155 | 8 | K-PB-401 | 25 | K-PC-074 | 63 | CONDUIT TEE (EX) 22mm | [9 empty] | 7 | 7 | EA
|  |  |  | K-PA-156 | 11 | K-PB-402 | 19 | K-PC-081 | 71 | REDUCER (EX) 28mm-22mm | [9 empty] | 7 | 7 | EA
|  |  |  | K-PA-157 | 8 | K-PB-403 | 17 | K-PC-082 | 71
|  |  |  | K-PA-158 | 11 | K-PB-404 | 15 | K-PC-083 | 85
|  |  |  | K-PA-165 | 8 | K-PB-413 | 28 | K-PC-084 | 85
|  |  |  | K-PA-166 | 11 | K-PB-414 | 27 | K-PC-091 | 22
|  |  |  | K-PA-167 | 8 | K-PB-423 | 42 | K-PC-092 | 22
|  |  |  | K-PA-168 | 11 | K-PB-432 | 45 | K-PC-093 | 13
|  |  |  | K-PA-176 | 8 | K-PB-433 | 44 | K-PC-094 | 13
|  |  |  | K-PA-177 | 11 | K-PB-653 | 6 | K-PC-102 | 38
|  |  |  | K-PA-284 | 10 | K-PB-661 | 25 | K-PC-103 | 38
|  |  |  | K-PA-285 | 8 | K-PB-662 | 9 | K-PC-111 | 63
|  |  |  | K-PA-296 | 10 | K-PB-663 | 8 | K-PC-112 | 63
|  |  |  | K-PA-297 | 8 | K-PB-671 | 33 | K-PC-114 | 46
|  |  |  | K-PA-305 | 10 | K-PB-672 | 28 | K-PC-115 | 46
|  |  |  | K-PA-306 | 8 | K-PB-673 | 27 | K-PC-121 | 85
|  |  |  | K-PA-307 | 10 | K-PB-681 | 40 | K-PC-122 | 85
|  |  |  | K-PA-308 | 8 | K-PB-682 | 39 | K-PC-131 | 13
|  |  |  | K-PA-315 | 10 | K-PB-691 | 57 | K-PC-132 | 13
|  |  |  | K-PA-316 | 8 | K-PB-692 | 56 | K-PC-141 | 21
|  |  |  | K-PA-317 | 10 | K-PB-693 | 49 | K-PC-142 | 21
|  |  |  | K-PA-318 | 8 | K-PB-807 | 7 | K-PC-144 | 38
|  |  |  | K-PA-326 | 10 | K-PB-817 | 7 | K-PC-145 | 38
|  |  |  | K-PA-327 | 8 | X-PB-805 | 10 | K-PC-152 | 47
|  |  |  | K-PA-808 | 10 | X-PB-806 | 10 | K-PC-153 | 47
|  |  |  | K-PA-816 | 23 | Total Result | 1687 | K-PC-161 | 63
|  |  |  | K-PA-823 | 6 |  |  | K-PC-162 | 63
|  |  |  | K-PA-825 | 8 |  |  | K-PC-173 | 85
|  |  |  | X-PA-001 | 38 |  |  | K-PC-174 | 85
|  |  |  | X-PA-002 | 13 |  |  | K-PC-181 | 4
|  |  |  | X-PA-011 | 21 |  |  | K-PC-201 | 13
|  |  |  | X-PA-021 | 46 |  |  | K-PC-202 | 13
|  |  |  | X-PA-031 | 63 |  |  | K-PC-211 | 38
|  |  |  | X-PA-041 | 85 |  |  | K-PC-212 | 38
|  |  |  | X-PA-042 | 71 |  |  | K-PC-213 | 21
|  |  |  | X-PA-051 | 13 |  |  | K-PC-214 | 21
|  |  |  | X-PA-061 | 21 |  |  | K-PC-221 | 63
|  |  |  | X-PA-062 | 38 |  |  | K-PC-222 | 63
|  |  |  | X-PA-071 | 46 |  |  | K-PC-223 | 46
|  |  |  | X-PA-072 | 63 |  |  | K-PC-224 | 46
|  |  |  | X-PA-081 | 71 |  |  | K-PC-231 | 85
|  |  |  | X-PA-082 | 85 |  |  | K-PC-232 | 85
|  |  |  | X-PA-091 | 22 |  |  | K-PC-233 | 71
|  |  |  | X-PA-092 | 13 |  |  | K-PC-234 | 71
|  |  |  | X-PA-101 | 46 |  |  | K-PC-241 | 13
|  |  |  | X-PA-102 | 38 |  |  | K-PC-242 | 13
|  |  |  | X-PA-111 | 63 |  |  | K-PC-251 | 21
|  |  |  | X-PA-121 | 85 |  |  | K-PC-252 | 21
|  |  |  | X-PA-122 | 71 |  |  | K-PC-253 | 38
|  |  |  | X-PA-131 | 13 |  |  | K-PC-254 | 38
|  |  |  | X-PA-141 | 21 |  |  | K-PC-261 | 46
|  |  |  | X-PA-151 | 38 |  |  | K-PC-262 | 46
|  |  |  | X-PA-152 | 47 |  |  | K-PC-263 | 63
|  |  |  | X-PA-161 | 63 |  |  | K-PC-264 | 63
|  |  |  | X-PA-162 | 71 |  |  | K-PC-271 | 71
|  |  |  | X-PA-171 | 85 |  |  | K-PC-272 | 71
|  |  |  | X-PA-181 | 4 |  |  | K-PC-273 | 85
|  |  |  | X-PA-201 | 13 |  |  | K-PC-274 | 85
|  |  |  | X-PA-211 | 38 |  |  | K-PC-282 | 13
|  |  |  | X-PA-212 | 21 |  |  | K-PC-283 | 13
|  |  |  | X-PA-221 | 63 |  |  | K-PC-291 | 39
|  |  |  | X-PA-222 | 46 |  |  | K-PC-292 | 39
|  |  |  | X-PA-231 | 85 |  |  | K-PC-294 | 21
|  |  |  | X-PA-232 | 71 |  |  | K-PC-295 | 21
|  |  |  | X-PA-241 | 13 |  |  | K-PC-302 | 46
|  |  |  | X-PA-251 | 21 |  |  | K-PC-303 | 46
|  |  |  | X-PA-252 | 38 |  |  | K-PC-313 | 63
|  |  |  | X-PA-261 | 46 |  |  | K-PC-314 | 63
|  |  |  | X-PA-262 | 63 |  |  | K-PC-322 | 85
|  |  |  | X-PA-271 | 71 |  |  | K-PC-323 | 85
|  |  |  | X-PA-272 | 85 |  |  | K-PC-331 | 13
|  |  |  | X-PA-281 | 13 |  |  | K-PC-332 | 13
|  |  |  | X-PA-291 | 21 |  |  | K-PC-341 | 21
|  |  |  | X-PA-301 | 46 |  |  | K-PC-342 | 21
|  |  |  | X-PA-302 | 39 |  |  | K-PC-343 | 38
|  |  |  | X-PA-311 | 71 |  |  | K-PC-344 | 38
|  |  |  | X-PA-312 | 63 |  |  | K-PC-351 | 46
|  |  |  | X-PA-321 | 85 |  |  | K-PC-352 | 46
|  |  |  | X-PA-331 | 13 |  |  | K-PC-353 | 63
|  |  |  | X-PA-341 | 21 |  |  | K-PC-354 | 63
|  |  |  | X-PA-342 | 38 |  |  | K-PC-363 | 85
|  |  |  | X-PA-351 | 46 |  |  | K-PC-364 | 85
|  |  |  | X-PA-352 | 63 |  |  | K-PC-371 | 4
|  |  |  | X-PA-361 | 71 |  |  | K-PC-411 | 24
|  |  |  | X-PA-362 | 85 |  |  | K-PC-412 | 24
|  |  |  | X-PA-371 | 4 |  |  | K-PC-421 | 41
|  |  |  | X-PA-401 | 30 |  |  | K-PC-422 | 41
|  |  |  | X-PA-402 | 10 |  |  | K-PC-501 | 16
|  |  |  | X-PA-411 | 24 |  |  | K-PC-502 | 16
|  |  |  | X-PA-412 | 25 |  |  | K-PC-503 | 26
|  |  |  | X-PA-421 | 42 |  |  | K-PC-504 | 26
|  |  |  | X-PA-422 | 15 |  |  | K-PC-511 | 43
|  |  |  | X-PA-423 | 22 |  |  | K-PC-512 | 43
|  |  |  | X-PA-431 | 41 |  |  | K-PC-651 | 48
|  |  |  | X-PA-451 | 15 |  |  | K-PC-652 | 48
|  |  |  | X-PA-452 | 22 |  |  | K-PC-721 | 66
|  |  |  | X-PA-501 | 16 |  |  | K-PC-722 | 66
|  |  |  | X-PA-511 | 26 |  |  | K-PC-723 | 49
|  |  |  | X-PA-512 | 43 |  |  | K-PC-724 | 49
|  |  |  | X-PA-621 | 24 |  |  | K-PC-741 | 85
|  |  |  | X-PA-622 | 23 |  |  | K-PC-742 | 91
|  |  |  | X-PA-651 | 48 |  |  | X-PC-751 | 80
|  |  |  | X-PA-652 | 6 |  |  | Total Result | 5578
|  |  |  | X-PA-661 | 16
|  |  |  | X-PA-662 | 11
|  |  |  | X-PA-671 | 33
|  |  |  | X-PA-672 | 25
|  |  |  | X-PA-681 | 45
|  |  |  | X-PA-682 | 38
|  |  |  | X-PA-683 | 7
|  |  |  | X-PA-691 | 49
|  |  |  | X-PA-692 | 33
|  |  |  | X-PA-721 | 49
|  |  |  | X-PA-731 | 75
|  |  |  | X-PA-732 | 66
|  |  |  | X-PA-742 | 91
|  |  |  | X-PA-801 | 8
|  |  |  | X-PA-802 | 8
|  |  |  | X-PA-803 | 7
|  |  |  | X-PA-804 | 7
|  |  |  | X-PA-807 | 10
|  |  |  | X-PA-811 | 6
|  |  |  | X-PA-901 | 8
|  |  |  | X-PA-902 | 12
|  |  |  | X-PA-903 | 14
|  |  |  | X-PA-904 | 19
|  |  |  | X-PA-905 | 21
|  |  |  | X-PA-906 | 26
|  |  |  | X-PA-907 | 28
|  |  |  | X-PA-908 | 32
|  |  |  | X-PA-909 | 34
|  |  |  | X-PA-910 | 8
|  |  |  | X-PA-911 | 6
|  |  |  | X-PA-912 | 8
|  |  |  | X-PA-913 | 10
|  |  |  | X-PA-914 | 14
|  |  |  | X-PA-915 | 16
|  |  |  | X-PA-916 | 21
|  |  |  | X-PA-917 | 23
|  |  |  | X-PA-918 | 28
|  |  |  | X-PA-919 | 30
|  |  |  | X-PA-920 | 34
|  |  |  | X-PA-921 | 36
|  |  |  | X-PA-922 | 8
|  |  |  | X-PA-923 | 6
|  |  |  | X-PA-924 | 78
|  |  |  | X-PA-925 | 18
|  |  |  | X-PA-926 | 20
|  |  |  | X-PA-927 | 24
|  |  |  | X-PA-928 | 31
|  |  |  | X-PA-929 | 37
|  |  |  | X-PA-930 | 44
|  |  |  | X-PA-931 | 51
|  |  |  | X-PA-932 | 23
|  |  |  | X-PA-933 | 28
|  |  |  | X-PA-934 | 30
|  |  |  | X-PA-935 | 34
|  |  |  | X-PA-936 | 44
|  |  |  | X-PA-937 | 20
|  |  |  | X-PA-938 | 20
|  |  |  | X-PA-939 | 19
|  |  |  | X-PA-940 | 21
|  |  |  | X-PA-941 | 26
|  |  |  | X-PA-942 | 28
|  |  |  | X-PA-943 | 32
|  |  |  | X-PA-944 | 34
|  |  |  | X-PA-945 | 8
|  |  |  | X-PA-946 | 6
|  |  |  | X-PA-947 | 8
|  |  |  | X-PA-948 | 12
|  |  |  | X-PA-949 | 14
|  |  |  | X-PA-950 | 19
|  |  |  | X-PA-951 | 21
|  |  |  | X-PA-952 | 26
|  |  |  | X-PA-953 | 28
|  |  |  | X-PA-954 | 32
|  |  |  | X-PA-955 | 34
|  |  |  | X-PA-956 | 8
|  |  |  | X-PA-957 | 6
|  |  |  | X-PA-958 | 8
|  |  |  | X-PA-959 | 12
|  |  |  | X-PA-960 | 14
|  |  |  | X-PA-961 | 19
|  |  |  | X-PA-962 | 21
|  |  |  | X-PA-963 | 26
|  |  |  | X-PA-964 | 28
|  |  |  | X-PA-965 | 32
|  |  |  | X-PA-966 | 34
|  |  |  | X-PA-967 | 8
|  |  |  | X-PA-968 | 6
|  |  |  | Total Result | 5713

## cable data (hidden)
Cable Spec. | O.D | S.A
22.9kV FR-CN/CO-W 1C-100㎟-P | 39 | 1193.985
0.6/1kV FR-CV 1C-185㎟-P | 24 | 452.16
0.6/1kV FR-CV 2C-4㎟-P | 13 | 132.665
0.6/1kV FR-CV 2C-6㎟-P | 14 | 153.86
0.6/1kV FR-CV 2C-10㎟-P | 17 | 226.865
0.6/1kV FR-CV 2C-16㎟-P | 18.5 | 268.6662
0.6/1kV FR-CV 2C-25㎟-P | 22 | 379.94
0.6/1kV FR-CV 2C-35㎟-P | 24 | 452.16
0.6/1kV FR-CV 3C-6㎟-P | 14.5 | 165.0462
0.6/1kV FR-CV 3C-10㎟-P | 18 | 254.34
0.6/1kV FR-CV 3C-25㎟-P | 23 | 415.265
0.6/1kV FR-CV 4C-6㎟-P | 16 | 200.96
0.6/1kV FR-CV 4C-10㎟-P | 20 | 314
0.6/1kV FR-CV 4C-25㎟-P | 26 | 530.66
0.6/1kV FR-CVV-S 3C-2.5㎟-C | 13.5 | 143.0662
0.6/1kV FR-CVV-S 4C-2.5㎟-C | 14.5 | 165.0462
0.6/1kV FR-CVV-S 10C-2.5㎟-C | 20.5 | 329.8963
0.6/1kV FR-3 2C-2.5㎟-C | 12 | 113.04
STP-CAT.5e 4P-24AWG㎟-C | 6.5 | 33.1662
- UL2919(RS485) 2P-24AWG㎟-S | 9 | 63.585
0.6/1kV FR-CVV-I/C AMS 1P-1.5㎟-S | 12 | 113.04
0.6/1kV FR-CVV-I/C AMS 1T-1.5㎟-S | 12.5 | 122.6562
0.6/1kV FR-CVV-I/C AMS 2P-1.5㎟-S | 16 | 200.96
0.6/1kV FR-CVV-I/C AMS 6P-1.5㎟-S | 21.5 | 362.8662
F.O CABLE SINGLE MODE 4C-0㎟-S | 9.5 | 70.8462